## Table S1
Table S1. Related works on decision support for deploying emergency healthcare hospitals
No. | Application context | Original facility type | Decision object | Decision method | Decision criteria | Ref.
1 | FSH for COVID-19 | Sports center, gymnasium, conference and exhibition center | Site selection | Spherical fuzzy PROMETHEE method | Transportation accessibility, environmental protection, spatial centrality, existing facility support, telecommunication reliability, capacity, retrofitting complexity, retrofitting budget | [1]
2 | FSH for pandemic outbreak | Unspecified candidate facilities in a city | Site selection | EWM-TOPSIS | Infection transmission risk, required patient capacity, and accessibility for critical patient transfer | [24]
3 | FSH for respiratory infectious diseases | An existed FSH | Layout optimization | Spatial flow impact factor model | Infection risk of clean zones, semi-contaminated zones, and contaminated zones. | [5]
4 | FSH for urban emergencies | Exhibition building | Evacuation efficiency | Scheme comparison based on Pathfinder simulation | Evacuation time, spatial congestion, flow rate through exists | [22]
5 | Field hospital for COVID-19 | Airport, community center, theme park, hospital (with/without ICU), emergency shelter, and stadium | Site selection | Enhanced 2-step floating catchment area method | Capacity, ICU demand level, and travel time for vulnerable census block groups | [25]
6 | Field hospital for earthquake | Urban parks, flat assembly ground | Site selection | VIKOR | Earthquake risk, local demographic concentration, available area, proximity to central districts, accessibility to existing hospitals, proximity to main arteries, congestion levels of adjacent arteries, transportation alternatives | [23]
7 | Field hospital for COVID-19 | Unspecified candidate facilities in several cities | Site selection | Nonlinear binary metaheuristic algorithm | Financial limitations, healthcare workforce availability, inventory limits of medical equipment and consumables | [26]
8 | Medical center for major public health events | Ordinary inpatient building | Layout design | Generative design based on genetic algorithm | Adjacency preference, infection risk score | [27]
9 | Emergency healthcare facilities for infectious disease | Any candidate facility | Semantic regulatory compliance checking | Augmented LLM with domain knowledge graph | Regulatory compliance | [28]
Note: PROMETHEE denotes Preference Ranking Organization Method for Enrichment Evaluation, VIKOR denotes VlseKriterijumska Optimizacija I Kompromisno Resenje, EWM denotes Entropy Weight Method, TOPSIS denotes Technique for Order Preference by Similarity to Ideal Solution.

## Table S2
Table S2. Related works on LLM-driven agents for decision support in deploying buildings
No. | Building type | Application scenario | System architecture | Technique |  | Knowledge source |  | Evaluation metric | Ref.
|  |  |  | RAG | Fine-tuning | Content | Form
1 | Large space buildings | Automated querying of building data | Single LLM | Adopted | Adopted | Brick models of 40 buildings | Text file | Query generation accuracy | [30]
2 | Unspecified | Automated safety risk management | Single LLM | Adopted | Adopted | 64,740 accident reports | Text file | ROUGE, BLEU, BERT Score, SBERT Score | [34]
3 | Concrete building | Automated compliance checking | Single LLM | Adopted | None | 3 related regulations | Knowledge base | Knowledge retrieval (Hit rate, Mean reciprocal rank), Response (Accuracy, Faithfulness) | [33]
4 | Emergency healthcare facilities | Decision support for delivering emergency healthcare facilities | Single LLM | Adopted | None | 19 related regulations | KG | Accuracy, Traceability, Relevance | [28]
5 | Unspecified | Building regulation question-answering | Single LLM | Adopted | None | 5 building design and construction regulations | Text file | Content existence (Precision, Recall, F1 score), Text similarity (ROUGE-1, ROUGE-2, ROUGE-L) | [35]
6 | Hotel building | Automatic modeling from text to BIM | MAS (Prompt enhancement, textual design generation, code generation, code optimization) | Adopted | None | 26 tool functions | Function | Final pass rate, Issue amount, Model adherence, Code generation accuracy | [37]
7 | Office building | Automated querying of BIM information | MAS (Query decomposition, entity alignment, query generation, answer generation) | Adopted | None | IFC files | KG | Sub-question generation, Query generation, Reasoning | [31]
8 | Campus dormitory | Accessible BIM interaction | MAS (Script generation, error checking, string encoding, code execution, process termination) | None | None | 6 skillset | Function | Accuracy, Execution success rate, Time, Cost | [20]
9 | Single family home | Automated compliance checking of BIM | MAS (Regulation interpretation, BIM information extraction, compliance checking, report generation) | None | None | Predefined IfcOpenShell script | Function | Rule interpretation (Precision, Recall, F1-score), Information extraction accuracy | [32]

## Table S3
Table S3. Profiles of the invited experts
No. | Working years | Department | Position
A1 | 20 | Department of infrastructure development in a hospital | Head
A2 | 17 | Department of infrastructure development in a hospital | Associate head
A3 | 16 | Department of infrastructure development in a hospital | Senior engineer
B1 | 19 | Emergency management bureau | Associate director
B2 | 21 | Emergency management bureau | Senior engineer
B3 | 18 | Emergency management bureau | Senior engineer
C1 | 16 | Large-scale building design company | Senior engineer
C2 | 19 | Large-scale building design company | Senior engineer
D1 | 18 | Large-scale building construction company | Senior engineer
D2 | 19 | Large-scale building construction company | Senior engineer
E1 | 25 | University | Professor
E2 | 19 | University | Professor
E3 | 18 | University | Professor

## Table S4
Table S4. Regulatory codes related to DFSH in China.
No. | Identifier | Title | Effective Date
1 | GB/T 45998-2025 | Facility management-Guidance on emergency preparedness and management of an epidemic | 2025-08-29
2 | WS/T 774-2021 | Standard of field disinfection evaluation during COVID-19 epidemic | 2021-02-20
3 | WS/T 698-2020 | Health protection guidelines in key places and units during COVID-19 epidemic | 2020-07-20
4 | WS 696-2020 | Hygienic specifications for operation and management of air-conditioning ventilation systems in office buildings and public places during COVID-19 epidemic | 2020-07-20
5 | WS 694-2020 | Health protection requirements of temporary special places for medical observation and treatment during COVID-19 epidemic | 2020-07-20
6 | T/CADBM 72-2023 | Technical standard for water supply and drainage for container-type shelter hospital | 2023-07-28
7 | T/CADBM 71-2023 | PVC floor coverings for container-type shelter hospital | 2023-07-20
8 | T/CADBM 70-2023 | PVC wallboard for container-type shelter hospital | 2023-07-20
9 | T/CECS 1226-2022 | Technical specification for transportation and treatment of demolition of Fangcang shelter hospital | 2023-05-01
10 | T/CECS 1206-2022 | Technical specification for large space building retrofitted Fangcang shelter hospital | 2022-11-22
11 | T/CECS 661-2020 | The design standard of infectious disease emergency medical facilities for novel coronavirus pneumonia | 2020-02-06
12 | T/CIQA 16-2021 | General technical specification of nucleic acid detecting laboratory cabin | 2021-04-01

## Table S5
Table S5. Testing set for DSS of DFSH
No. | Difficulty Level | Question | Answer | Graph nodes of Spatial KG | Graph nodes of Regulatory KG
1 | Level-1 | During the conversion, does Storage S1 need to be equipped specifically for the controlled storage of contaminated items? | Yes. General-purpose supply planning for pandemic response must include specific provisions and allocations for the controlled storage of contaminated items to safely manage infectious risks. | IfcSpace_S1 | Clause 7.1.3 of GB/T 45998-2025
2 | Level-1 | Should the existing cleaning cart in Storage S2 be stocked with specific disinfectants determined by national or international health guidelines? | Yes. The required materials for pandemic response must include cleaning agents, disinfectants, and neutralizers, and their specific types should be identified based on guidance from established national and international health resources. | Equipment_CleaningCart_S2 | Clause 7.1.3 of GB/T 45998-2025
3 | Level-1 | When converting the badminton hall into a shelter hospital, does the exterior door of the corridor require intervention regarding its normal access control parameters? | Yes. Since the facility's operational purpose has changed, the entrance/exit control (such as limiting personnel, changing access routes, and enforcing health checks) must be addressed to adapt to the new clinical parameters. | Connection_ExtDoor_W59 | Clause 8.3.1 of GB/T 45998-2025
4 | Level-1 | When planning the disinfection efficacy evaluation for the restroom, is it necessary to designate the existing toilets as key sampling objects and collect at least two samples from them? | Yes. Toilets are high-touch surfaces that must be prioritized as key sampling targets during evaluations, and a minimum of two samples must be collected for each specific category of object to ensure statistical validity. | Equipment_Toilet_1 | Clause 6.3.1 of WS/T 774-2021
5 | Level-1 | Should the handle of the door connecting the main hall and the storage room be included as a priority sampling point, contributing to a minimum total of 30 test samples across the facility? | Yes. Door handles are explicitly designated as primary targets for surface sampling, and the comprehensive evaluation across the entire facility must accumulate a total of no less than 30 test samples to meet baseline testing standards. | Connection_Door_W4 | Clause 6.3.1 of WS/T 774-2021
6 | Level-1 | When evaluating the air disinfection efficacy in the expansive main hall, is it justifiable to establish more than 5 sampling points, up to a maximum of 30? | Yes. For large spaces with an indoor area exceeding 60 square meters, the number of sampling points can be increased based on actual environmental needs and calculated by a specific formula, with a maximum limit of 30 points. | IfcSpace_M1 | Clause 6.3.2 of WS/T 774-2021
7 | Level-1 | When using the plate exposure method in Storage Room S3, should the outermost sampling points be positioned exactly 1 meter away from the room's boundaries? | Yes. Regardless of whether the room's footprint dictates a 3-point diagonal layout or a 5-point layout, the outermost or corner sampling points must be strictly placed at a distance of 1 meter from the walls. | IfcSpace_S3 | Clause 6.3.2 of WS/T 774-2021
8 | Level-1 | During the operation of the shelter hospital, should the cleaning regimen for the door connecting the main corridor to the main hall be adjusted to a higher frequency? | Yes. Door handles are high-frequency contact surfaces, and the cleaning and disinfection frequency for such objects must be explicitly increased during pandemic response operations to mitigate cross-infection risks. | Connection_Door_W13 | Clause 5.1.3 of WS/T 698-2020
9 | Level-1 | Is the existing floor drain in the restroom suitable to be retained for the contaminated zone without modification? | Yes. The properties of the existing floor drain indicate it is equipped with a U-shaped water seal, strictly complying with the safety mandate in Clause 5.1.2.6. | IfcSanitaryTerminal_R1_Drain | Clause 5.1.2.6 of WS 696-2020
10 | Level-1 | Does the existing HVAC air handling unit in the main hall meet the condensate drainage safety requirements for an infectious disease facility? | Yes. The unit's condensate drain pipe already possesses a U-shaped water seal, which adheres to the plumbing safety requirements specified in Clause 5.1.2.6. | IfcAirTerminal_M1_AHU | Clause 5.1.2.6 of WS 696-2020
11 | Level-1 | When configuring the air conditioning system for the main hall, is it mandatory to install protective nets and primary filters on the fresh air intakes? | Yes. Fresh air inlets must be equipped with protective nets and primary filters to prevent external physical contaminants and large particulates from entering the indoor ventilation system. | MEP_HVAC_M1_2 | Clause 6.1.3 of WS 696-2020
12 | Level-1 | Should the fresh air supply drawn from the outdoor environment be structurally separated from any existing open cooling towers located outside the building? | Yes. To ensure the safety of the incoming air supply, fresh air inlets must maintain a safe distance from open cooling towers and any other external environmental pollution sources. | IfcSpace_Outdoor | Clause 6.1.3 of WS 696-2020
13 | Level-1 | When establishing the main hall as the primary patient ward, must it be strictly classified and operated as a designated contaminated zone within the facility's overall layout? | Yes. The facility must be strictly operated according to a zoning strategy comprising contaminated, semi-contaminated, and clean zones, and a patient ward inherently falls under the contaminated classification. | IfcSpace_M1 | Clause 4.1.3.1 of WS 694-2020
14 | Level-1 | If the existing main corridor is proposed to handle both medical staff entry and patient admission, is a physical partition mandatory within this space? | Yes. The operational layout must feature designated clean and contaminated corridors, and these two pathways must be completely separated to prevent any risk of cross-contamination. | IfcSpace_C1 | Clause 4.1.3.1 of WS 694-2020
15 | Level-1 | When establishing patient wards in the main hall, is it compliant to design a designated male-only zone containing 45 beds? | Yes. The ward area must implement strict gender zoning, and the planned capacity of 45 beds successfully complies with the mandate that no single zone shall exceed 50 beds. | IfcSpace_M1 | Clause 4.1.3.4 of WS 694-2020
16 | Level-1 | During the bed configuration phase, if the existing badminton spectator chairs are retained near the beds, is it still mandatory to additionally procure and place a bedside table and a storage box? | Yes. Regardless of existing seating facilities, each individual patient bed must be explicitly provisioned with standard personal necessities, which strictly includes bedding, a bedside table, a storage box, and a trash can. | Equipment_Chair_1 | Clause 4.1.3.4 of WS 694-2020
17 | Level-1 | When converting the main corridor, if the original floor surface is assessed as lacking adequate slip resistance, is the installation of temporary anti-slip mats required? | Yes. Temporary special facilities must implement anti-slip measures, and if the floor surfaces in circulation areas like corridors are untreated, laying temporary anti-slip mats is strictly mandatory. | Boundary_Floor_C1 | Clause 4.4.3 of WS 694-2020
18 | Level-1 | Does the floor area around the existing sinks in the restroom require specific physical interventions if it currently lacks a textured anti-slip finish? | Yes. Washroom zones are highly prone to water accumulation, and safety regulations mandate that temporary anti-slip mats must be laid down if the original floor lacks proper anti-slip treatment. | Equipment_Sink_1 | Clause 4.4.3 of WS 694-2020
19 | Level-1 | When deploying containerized ward modules inside the main hall, is it recommended to connect their primary water supply directly to the existing municipal water network of the building? | Yes. To ensure a stable and continuous flow of safe water for medical operations, the water supply system for containerized facilities should ideally be sourced directly from the municipal water network. | IfcSpace_M1 | Clause 4.1.1 of T/CADBM 72-2023
20 | Level-1 | If a containerized triage unit is placed in the outdoor area, does its independent water supply design need to incorporate specific measures to guarantee environmental protection? | Yes. The design of any water supply system for containerized modules must strictly integrate comprehensive measures that satisfy the requirements for both environmental protection and operational safety. | IfcSpace_Outdoor | Clause 4.1.1 of T/CADBM 72-2023
21 | Level-1 | When upgrading the main hall into a contaminated ward zone, must the condensate drain pipe of its air conditioning unit be configured to discharge indirectly into the sewage system? | Yes. The main hall acts as a contaminated zone, and the condensate water from its air conditioning units must be discharged indirectly into the sewage pipe to safely manage infectious risks and prevent gas backflow. | MEP_HVAC_M1_3 | Clause 4.3.4 of T/CADBM 72-2023
22 | Level-1 | If Storage S4 is retrofitted into a buffer zone between the clean and contaminated corridors, is it mandatory to route its HVAC condensate water to the wastewater line using an indirect drainage method? | Yes. For any space functioning as a buffer zone, the air conditioning condensate must be managed via indirect drainage and routed specifically into the sewage piping network to ensure stringent infection control. | MEP_HVAC_S4 | Clause 4.3.4 of T/CADBM 72-2023
23 | Level-1 | When receiving materials for the containerized modules, is it compliant to store the PVC flooring rolls upright in batches within the well-ventilated Storage S5 at a controlled temperature of 25°C? | Yes. PVC flooring rolls are strictly required to be stored upright in batches within a dry, clean, and ventilated indoor warehouse environment where the ambient temperature is maintained below 40°C. | IfcSpace_S5 | Clause 8.3 of T/CADBM 71-2023
24 | Level-1 | When storing PVC wall panels for the containerized modules in Storage S1, is it compliant to stack them flat on the floor with a total stack height of 1.5 meters? | Yes. PVC wall panels must be stored flat indoors, and the stack height is strictly advised not to exceed 2 meters to ensure material stability and safety. | IfcSpace_S1 | Clause 8.3 of T/CADBM 70-2023
25 | Level-1 | If multiple specifications of PVC wall panels are kept in Storage S3, must the facility management team sort them into separate stacks and attach specific identification labels to each pile? | Yes. Storage regulations mandate that materials must be stacked separately according to their specific categories and specifications, and each individual stack must have corresponding identification markings. | IfcSpace_S3 | Clause 8.3 of T/CADBM 70-2023
26 | Level-1 | During the dismantling phase of Storage S4, is it correct to first remove the storage cabinets before taking down the temporary partition walls? | Yes. The dismantling sequence mandates that furniture and household items must be removed first before proceeding to dismantle any room partitions and their accessories. | Equipment_Cabinet_A_S4 | Clause 6.1.4 of T/CECS 1226-2022
27 | Level-1 | In the process of restoring the restroom facility, should the sanitary sinks and their drainage pipes be removed before dismantling any newly installed isolation partitions? | Yes. Water supply and drainage facilities must be fully removed in the second step of the sequence, strictly prior to the dismantling of any space partitions. | Equipment_Sink_3 | Clause 6.1.4 of T/CECS 1226-2022
28 | Level-1 | When clearing Locker Room L2, is it compliant to first remove the table and chair sets, and subsequently disconnect and remove the room's lighting fixtures? | Yes. The established sequence correctly prioritizes the removal of furniture as the first step, followed immediately by the removal of electrical facilities like lighting fixtures. | Equipment_TableChairSet_L2 | Clause 6.1.4 of T/CECS 1226-2022
29 | Level-1 | When the facility is decommissioned, must the original wall separating the main hall and the locker room be fully restored to its pre-conversion condition? | Yes. The restoration of existing buildings must explicitly include the complete recovery of all original wall structures and their surface finishes. | Boundary_W55 | Clause 6.3.2 of T/CECS 1226-2022
30 | Level-1 | During the post-pandemic restoration phase of the main hall, is the repair and replacement of any broken exterior window glass mandated by the standard? | Yes. The decommissioning and restoration of existing structures must comprehensively include the physical restoration of all exterior windows and glass components. | Connection_ExtWin_W25 | Clause 6.3.2 of T/CECS 1226-2022
31 | Level-1 | When restoring the main hall post-pandemic, must the original HVAC terminals be fully restored and commissioned to a qualified operational state? | Yes. The restoration of building equipment explicitly includes HVAC systems, and they must be fully commissioned and tested to meet qualified operational standards after reinstallation. | MEP_HVAC_M1_5 | Clause 6.3.3 of T/CECS 1226-2022
32 | Level-1 | After the temporary containerized washrooms are removed, does the original restroom's plumbing and toilet system require comprehensive recommissioning before reopening the facility? | Yes. The restoration of water supply and drainage facilities is mandatory, and the plumbing system must be fully commissioned to a qualified status before resuming normal operations. | Equipment_Toilet_3 | Clause 6.3.3 of T/CECS 1226-2022
33 | Level-1 | During the dismantling of the restroom facility, must the wastewater generated from flushing and removing the existing toilets be routed through the shelter's on-site treatment facility before discharge? | Yes. Wastewater generated during the decommissioning of sanitary fixtures must undergo pre-treatment using the shelter's existing wastewater treatment facilities before it can be safely discharged. | Equipment_Toilet_4 | Clause 9.1.3 of T/CECS 1226-2022
34 | Level-1 | After pre-treating the wastewater generated from dismantling the restroom sinks, should the treated effluent be directed specifically into the municipal sewage piping network? | Yes. Once the wastewater from dismantling plumbing fixtures has been properly pre-treated by the facility's existing systems, it must be safely and legally discharged into the municipal sewage network. | Equipment_Sink_4 | Clause 9.1.3 of T/CECS 1226-2022
35 | Level-1 | Should the fire protection design of the Fangcang hospital fully utilize the existing safe evacuation width provided by the main hall's exterior door? | Yes. The fire safety design must fully integrate and utilize the existing large space building's original fire compartments, safe evacuation distances, and evacuation widths to ensure proper egress. | Connection_ExtDoor_W7 | Clause 3.0.8 of T/CECS 1206-2022
36 | Level-1 | To ensure operational safety, is it a mandatory requirement to have fire trucks stationed on standby in the outdoor area 24 hours a day? | Yes. To guarantee absolute fire safety during the shelter hospital's operational period, stringent measures must be implemented, which strictly include maintaining fire trucks on 24-hour outdoor standby alongside strengthened fire patrols. | IfcSpace_Outdoor | Clause 3.0.8 of T/CECS 1206-2022
37 | Level-1 | When designating Locker Room L1 as a workspace for medical and support staff, should this area be strictly classified as a clean zone within the overall site plan? | Yes. Workspaces designated for medical and other staff, as well as clean support rooms, must be strictly classified as the clean zone within the facility's overall layout. | IfcSpace_L1 | Clause 4.0.4 of T/CECS 1206-2022
38 | Level-1 | If the main hall's exterior door is designated as the contaminated entrance and the corridor's door serves as the clean entrance, must the physical distance between them be at least 20 meters? | Yes. The clean and contaminated zones must have separately established entrances and exits, and the mutual distance between them must strictly be no less than 20 meters to prevent cross-contamination. | Connection_ExtDoor_W7 | Clause 4.0.4 of T/CECS 1206-2022
39 | Level-1 | When assessing the outdoor area, if the contaminated main hall is separated from adjacent external buildings by a landscaped green belt, is a minimum isolation distance of 20 meters sufficient? | Yes. When landscaped greening conditions are met, the isolation distance between buildings and facilities in the contaminated zone and adjacent buildings outside the hospital perimeter is permitted to be no less than 20 meters. | IfcSpace_Outdoor | Clause 4.0.4 of T/CECS 1206-2022
40 | Level-1 | When deploying mobile sanitary facilities for patients in the outdoor area, should they be positioned downwind of the prevailing wind and kept away from any catering or water supply points? | Yes. Patient sanitary facilities should ideally be constructed or placed outdoors in the contaminated zone, specifically positioned downwind of the local prevailing wind and safely distanced from dining areas and water supply points. | IfcSpace_Outdoor | Clause 5.1.3 of T/CECS 1206-2022
41 | Level-1 | If Locker Room L1 is converted into a shower and washroom specifically for medical staff, must this facility be structurally and operationally separated from the sanitary facilities utilized by the patients? | Yes. The restrooms, shower rooms, and washing areas designated for patients must be completely separated from those used by medical staff and other personnel to fundamentally prevent cross-infection. | IfcSpace_L1 | Clause 5.1.3 of T/CECS 1206-2022
42 | Level-1 | When repurposing the main hall into a densely populated patient ward, is it recommended to protect its original floor surface by applying dry-laid, flame-retardant roll materials? | Yes. For densely populated indoor spaces and areas with a high risk of contamination, the original floors should be protected using dry-laid roll materials that are strictly composed of flame-retardant or non-combustible eco-friendly materials. | Boundary_Floor_M1 | Clause 5.1.9 of T/CECS 1206-2022
43 | Level-1 | If Locker Room L1 is configured as the dedicated entrance sanitary passage for medical staff into the contaminated main hall, must a completely different space be assigned for their exit route? | Yes. Sanitary passages for entering and exiting the contaminated zone must be established as completely separate physical routes; a designated entrance facility cannot simultaneously serve as an exit passage. | IfcSpace_L1 | Clause 5.4.2 of T/CECS 1206-2022
44 | Level-1 | When integrating Storage S2 into the infection control layout, is it recommended to convert it into a dedicated sanitary passage exclusively for cleaning and logistical workers? | Yes. To minimize cross-contamination risks among different working groups, it is strongly advised that the sanitary passages used by medical personnel and those used by other operational staff are set up separately. | IfcSpace_S2 | Clause 5.4.2 of T/CECS 1206-2022
45 | Level-1 | When converting the main hall into a patient treatment area, is it compliant to officially classify this entire space as the designated isolation zone? | Yes. Emergency medical facilities must strictly define their layout according to infectious disease protocols, and the basic zoning mandates the establishment of an isolation zone, which fundamentally includes the contaminated patient treatment areas. | IfcSpace_M1 | Clause 4.0.5 of T/CECS 661-2020
46 | Level-1 | If Storage S4 is located between a clean administrative area and a semi-contaminated testing area, is it recommended to repurpose it specifically as an intermediate buffer room? | Yes. To safely manage the transition between different functional areas, corresponding buffer rooms or sanitary passages must be explicitly set up between adjacent zones of differing cleanliness levels. | IfcSpace_S4 | Clause 4.0.5 of T/CECS 661-2020
47 | Level-1 | When converting the main hall into a contaminated patient ward, must a dedicated mechanical ventilation system be explicitly installed for this specific area? | Yes. Emergency medical facilities are strictly required to be equipped with mechanical ventilation, and the supply and exhaust systems must be established as completely independent systems dedicated to the contaminated zone. | MEP_HVAC_M1_6 | Clause 7.0.1 of T/CECS 661-2020
48 | Level-1 | If Locker Room L1 is designated as a semi-clean staff area, must its indoor static air pressure be maintained at a higher level than that of the adjacent semi-contaminated buffer rooms? | Yes. To ensure a safe directional airflow, the ventilation design must strictly maintain a pressure gradient where the static air pressure sequentially decreases from the semi-clean zone down to the semi-contaminated zone. | IfcSpace_L1 | Clause 7.0.1 of T/CECS 661-2020
49 | Level-1 | When deploying a containerized nucleic acid testing laboratory inside the main hall, must its ventilation system operate completely independently from the building's original central air conditioning? | Yes. The ventilation system of the testing cabin must be established completely independently to strictly prevent airborne infectious agents and gaseous pollutants from diffusing into other work areas within the large-space building. | IfcSpace_M1 | Clause 5.4.1.4 of T/CIQA 16-2021
50 | Level-1 | Within the containerized testing lab deployed in the main hall, must the reagent preparation zone and the nucleic acid amplification zone be equipped with their own separate ventilation systems? | Yes. Different protection zones within the testing laboratory are strictly required to be equipped with their own independent ventilation systems to eliminate any risk of cross-contamination between distinct testing phases. | MEP_HVAC_M1_7 | Clause 5.4.1.4 of T/CIQA 16-2021
51 | Level-1 | When planning the material inventory for the main corridor (C1), can the facility management team finalize the list of required pandemic supplies based solely on their experience managing the sports facility? | No. The materials needed to respond to an outbreak cannot be determined by the facility team alone; they must be identified following the guidance of established national and international resources, such as the WHO or government health agencies. | IfcSpace_C1 | Clause 7.1.3 of GB/T 45998-2025
52 | Level-1 | Is it acceptable to designate Locker Room L1 for medical staff preparation without pre-planning a dedicated inventory for personal protective equipment (PPE)? | No. The pre-planned list of essential supplies for emergency response must explicitly include personal protective equipment alongside other basic disposal tools and supplies. | IfcSpace_L1 | Clause 7.1.3 of GB/T 45998-2025
53 | Level-1 | Since the main hall is repurposed for centralized patient isolation, is it acceptable to keep the original operating parameters of its existing HVAC terminals unchanged? | No. When a facility's normal operation changes, issues related to building systems, specifically including ventilation services, should be resolved and adjusted to meet the new environmental safety requirements. | MEP_HVAC_M1_1 | Clause 8.3.1 of GB/T 45998-2025
54 | Level-1 | Is the original cleaning regimen and water supply system for the existing restroom sufficient for the new Fangcang operation without any parameter review? | No. If a facility's normal operating parameters change, the building systems and services, such as water supply and cleaning regimens, must be reviewed and resolved to support the new intensive operational demands. | IfcSpace_R1 | Clause 8.3.1 of GB/T 45998-2025
55 | Level-1 | During the evaluation of natural bacteria reduction on the main hall floor, is it permitted to collect both the pre-disinfection and post-disinfection samples from the exact same swabbed area? | No. When evaluating natural bacteria, pre- and post-disinfection sampling points must be established as pairs on the same surface type, but samples must never be collected twice from the exact same localized area. | Boundary_Floor_M1 | Clause 6.3.1 of WS/T 774-2021
56 | Level-1 | For the structural corners in the storage room where disinfection factors are hard to reach, is it acceptable to take only one sample or completely omit them from the sampling plan? | No. Additional sampling points or indicator microbial carriers must be deployed in hard-to-reach areas such as corners, and every targeted object category must strictly have no fewer than two samples collected. | Boundary_Col_Corner_S1 | Clause 6.3.1 of WS/T 774-2021
57 | Level-1 | Assuming Locker Room L2 has a footprint exceeding 30 square meters, is it permissible to set only 3 sampling points along its diagonal for the air disinfection evaluation? | No. If the indoor area is greater than 30 square meters, a 5-point layout encompassing the four corners and the center must be utilized, rather than the 3-point diagonal configuration reserved for smaller rooms. | IfcSpace_L2 | Clause 6.3.2 of WS/T 774-2021
58 | Level-1 | To save functional space during the air sampling process in the restroom, is it acceptable to place the sampling plates directly against the partition wall separating it from the corridor? | No. The sampling points positioned at the corners or outer edges of a room must maintain a mandatory clearance distance of 1 meter away from the walls, and cannot be placed directly against any partition boundary. | Boundary_W16 | Clause 6.3.2 of WS/T 774-2021
59 | Level-1 | Is it compliant to maintain the badminton hall's original standard cleaning schedule and ventilation rates for the shared restroom facility? | No. The frequency of ventilation and the cleaning and disinfection regimens for shared public facilities, specifically including public restrooms, must be actively increased rather than maintained at baseline levels. | IfcSpace_R1 | Clause 5.1.3 of WS/T 698-2020
60 | Level-1 | Is it permissible to locate the new fresh air intake for the main hall immediately adjacent to the existing exhaust fan of the restroom to simplify ductwork routing? | No. Fresh air inlets must be situated far away from building exhaust outlets and other potential pollution sources to fundamentally prevent cross-contamination of the intake air. | MEP_ExhaustFan_R1_1 | Clause 6.1.3 of WS 696-2020
61 | Level-1 | If the exterior window of Locker Room L1 is utilized as a natural fresh air inlet, is it acceptable to leave it completely open without any screening or filtration devices? | No. Any designated fresh air inlet must be fitted with protective nets and primary filters, regardless of whether it is a mechanical ventilation duct or an adapted natural ventilation opening. | Connection_ExtWin_W51 | Clause 6.1.3 of WS 696-2020
62 | Level-1 | Is it acceptable for medical staff in clean scrubs and newly admitted patients to share the same exterior door of the corridor if they arrive at completely different times? | No. The facility must operate with distinct clean and contaminated corridors, and these two pathways must remain completely separated at all times without any shared access points or temporal multiplexing. | Connection_ExtDoor_W59 | Clause 4.1.3.1 of WS 694-2020
63 | Level-1 | Can medical personnel directly enter the patient ward from the outdoor area through the main hall's dedicated exterior door to save operational time? | Can medical personnel directly enter the patient ward from the outdoor area through the main hall's dedicated exterior door to save operational time? | Connection_ExtDoor_W7 | Clause 4.1.3.1 of WS 694-2020
64 | Level-1 | Can the existing main hall be planned as a single, undivided patient ward zone accommodating 60 beds? | No. The planned capacity of 60 beds in a single zone violates Clause 4.1.3.4, which mandates that each ward zone must not exceed 50 beds. A spatial partition strategy is required. | IfcSpace_M1 | Clause 4.1.3.4 of WS 694-2020
65 | Level-1 | To maximize patient admission, is it permitted to arrange the beds alongside the internal structural columns with a clearance distance of 1.0 meter between them? | No. To ensure safe droplet isolation and adequate nursing access, the physical spacing between any two adjacent patient beds must strictly be greater than 1.2 meters. | Boundary_Col_M1_Extra_1 | Clause 4.1.3.4 of WS 694-2020
66 | Level-1 | Can a temporary mixed-gender observation zone consisting of 20 beds be set up directly on the main hall floor if all beds are spaced 1.5 meters apart? | No. Although the bed spacing and the total capacity within the zone meet the numerical requirements, the ward area must strictly enforce gender segregation, explicitly prohibiting any mixed-gender patient zones. | Boundary_Floor_M1 | Clause 4.1.3.4 of WS 694-2020
67 | Level-1 | If Locker Room L1 is repurposed as a temporary shower room for medical staff, is it acceptable to keep its original smooth flooring exposed to allow for rapid water drainage? | No. The requirement for slip prevention supersedes drainage convenience; if a space is utilized as a shower room and its floor is untreated, temporary anti-slip mats must be installed to prevent hazards. | Boundary_Floor_L1 | Clause 4.4.3 of WS 694-2020
68 | Level-1 | To expedite the daily mopping and disinfection process, can the facility management team choose to omit anti-slip mats around the urinals in the shared restroom? | No. Cleaning efficiency cannot compromise patient and staff safety standards; high-risk wet areas like toilets must incorporate anti-slip measures, necessitating the use of temporary mats on untreated floors. | Equipment_Urinal_1 | Clause 4.4.3 of WS 694-2020
69 | Level-1 | To rapidly retrofit the existing washroom with containerized sanitation modules, is it acceptable to bypass water-saving sink fixtures if it significantly speeds up the installation process? | No. Regardless of the urgency of the installation, the design of the water supply system must inherently satisfy the mandate for water conservation alongside reliability and safety. | Equipment_Sink_2 | Clause 4.1.1 ofT/CADBM 72-2023
70 | Level-1 | Can the containerized toilet modules rely solely on a temporary, unverified external water tank to cut initial deployment costs, rather than connecting to a stable municipal supply? | No. Relying on an unverified temporary source violates the mandate for a highly reliable water supply; containerized systems must be designed for reliability and should ideally utilize the stable municipal water network. | Equipment_Toilet_2 | Clause 4.1.1 ofT/CADBM 72-2023
71 | Level-1 | To simplify plumbing in the retrofitted restroom, is it permitted to securely hardwire and directly connect the air conditioner's condensate drain line into the main sewage stack? | No. Direct connection poses a severe risk of contaminated sewage gases backing up into the ventilation system. The condensate water in contaminated zones must be discharged into the sewage pipe strictly through indirect drainage methods, such as utilizing an air gap. | MEP_HVAC_R1 | Clause 4.3.4 ofT/CADBM 72-2023
72 | Level-1 | Can the condensate water generated by the air terminals in the main hall be diverted into the building's rainwater drainage system to reduce the hydraulic load on the sewage treatment plant? | No. Condensate water generated in a contaminated ward zone carries potential viral loads and must never be mixed with rainwater. It is mandatory to discharge this condensate strictly into the designated sewage pipes. | MEP_HVAC_M1_4 | Clause 4.3.4 ofT/CADBM 72-2023
73 | Level-1 | To maximize vertical clearance in Storage S2, is it permissible to stack the reserve PVC flooring rolls horizontally flat on the ground if the room temperature is kept cool? | No. Regardless of optimal temperature and cleanliness, PVC flooring rolls must be stored strictly in an upright position rather than laid flat horizontally to ensure material integrity and prevent deformation. | IfcSpace_S2 | Clause 8.3 of T/CADBM 71-2023
74 | Level-1 | To free up indoor workspace during the conversion, is it permissible to temporarily stack the PVC wall panels in the outdoor area if they are covered with a waterproof tarp? | No. The PVC wall panels are strictly required to be stored indoors during the storage process, regardless of whether external protective coverings are applied. | IfcSpace_Outdoor | Clause 8.3 of T/CADBM 70-2023
75 | Level-1 | Due to the narrow spatial constraints in the main corridor, can workers temporarily step on the stacked PVC wall panels to access overhead lighting fixtures? | No. During the storage and handling process, stepping or trampling on the PVC wall panels is strictly prohibited to prevent material contamination and structural damage. | IfcSpace_C1 | Clause 8.3 of T/CADBM 70-2023
76 | Level-1 | When decommissioning the main corridor, is it acceptable to demolish the partition walls first and then remove the fire extinguishers? | No. The standard dismantling sequence dictates that fire protection and electrical facilities must be entirely removed before any partitions or structural accessories are dismantled. | Equipment_FireExtinguisher_C1 | Clause 6.1.4 of T/CECS 1226-2022
77 | Level-1 | To expedite the decommissioning of the main hall, can the demolition team dismantle the HVAC terminals while the patient chairs and beds are still left inside? | No. The proper dismantling order requires that all furniture and household appliances be completely cleared out first, before any HVAC, plumbing, or electrical equipment is removed. | Equipment_Chair_2 | Clause 6.1.4 of T/CECS 1226-2022
78 | Level-1 | During the final decommissioning of the corridor, is it permitted to demolish the newly built structural additions before completely removing the corridor's lighting and electrical wiring? | No. The demolition of newly built or modified structures is the final step in the sequence and must only occur after all electrical facilities and partitions have been safely removed. | MEP_Light_C1_1 | Clause 6.1.4 of T/CECS 1226-2022
79 | Level-1 | To reduce overall decommissioning costs, is it acceptable to leave the damaged interior doors between the main hall and the storage rooms unrestored? | No. The mandatory restoration scope for existing buildings strictly requires the full repair and recovery of all doors and windows to their original state. | Connection_Door_W6 | Clause 6.3.2 of T/CECS 1226-2022
80 | Level-1 | Can the restoration team skip the cosmetic repair of the main corridor's floor if the underlying structural concrete slab remains functionally intact? | No. The restoration standard explicitly mandates that the recovery process must cover surface finishes and floors, meaning cosmetic and functional floor damages must both be repaired. | Boundary_Floor_C1 | Clause 6.3.2 of T/CECS 1226-2022
81 | Level-1 | During the decommissioning of the main corridor, is it sufficient to merely reinstall the fire extinguishers without conducting any final operational testing? | No. The restoration of fire protection facilities must include both the physical reinstallation and a mandatory commissioning phase to ensure the entire system operates at a qualified status. | Equipment_FireExtinguisher_C1 | Clause 6.3.3 of T/CECS 1226-2022
82 | Level-1 | To accelerate the reopening of the badminton hall, can the restoration team skip the formal commissioning of the main hall's electrical lighting system once the fixtures are physically mounted? | No. Physical reinstallation alone is incomplete; electrical systems must be formally commissioned and verified to have reached a qualified status following their physical restoration. | MEP_Light_M1_1 | Clause 6.3.3 of T/CECS 1226-2022
83 | Level-1 | To accelerate the dismantling process, can the wastewater generated from the site be discharged directly into the outdoor municipal rainwater drains if it looks visually clean? | No. Visual inspection is insufficient and dangerous; all wastewater generated during dismantling must be pre-treated through the facility's dedicated sewage treatment system and discharged strictly into the municipal sewage network, never into rainwater drains. | IfcSpace_Outdoor | Clause 9.1.3 of T/CECS 1226-2022
84 | Level-1 | Can the contaminated wastewater collected in the cleaning carts during the final decommissioning cleanup be trucked away untreated to a standard landfill to bypass the shelter's treatment system? | No. All wastewater generated during the dismantling and final cleanup phase must mandatorily utilize the shelter's existing on-site wastewater treatment facilities for pre-treatment prior to any external discharge or disposal. | Equipment_CleaningCart_S2 | Clause 9.1.3 of T/CECS 1226-2022
85 | Level-1 | Is it prohibited to add new mobile fire extinguishers in the main corridor to avoid interfering with the original building's fixed fire suppression system? | No. Based on fire safety assessments and testing results, the facility is explicitly permitted and encouraged to deploy additional mobile fire extinguishing equipment to enhance the overall safety of the large space building. | Equipment_FireExtinguisher_C1 | Clause 3.0.8 of T/CECS 1206-2022
86 | Level-1 | Can the facility management team ignore the original fire compartment areas of the main hall since the space is being completely repurposed as a temporary emergency ward? | No. The fire protection design for the temporary facility must not disregard existing structural constraints; rather, it must fully combine and utilize the original large space building's fire compartment areas and existing fire protection facilities. | IfcSpace_M1 | Clause 3.0.8 of T/CECS 1206-2022
87 | Level-1 | Since the main hall is repurposed as a patient admission and treatment area, can it be classified as a clean zone if high-efficiency air purifiers are installed indoors? | No. Regardless of internal equipment, areas used for patient admission and treatment, as well as pre-hospital areas, are inherently mandated to be classified strictly as contaminated zones. | IfcSpace_M1 | Clause 4.0.4 of T/CECS 1206-2022
88 | Level-1 | To minimize the outdoor walking distance for medical staff, is it permitted to establish the clean zone entrance only 10 meters away from the corridor's exterior door used by patients? | No. The entrances and exits for the clean and contaminated zones must be distinctly separated, and the linear distance between them must not be reduced below the 20-meter minimum safety threshold. | Connection_ExtDoor_W59 | Clause 4.0.4 of T/CECS 1206-2022
89 | Level-1 | If the outdoor paved area outside the main hall's exterior wall lacks any greenery, is it acceptable to position the contaminated ward 25 meters away from the nearest adjacent residential building? | No. In the absence of landscaping or greenery conditions, the required isolation distance between the contaminated zone buildings and external adjacent buildings must be strictly increased to a minimum of 30 meters. | Boundary_W7 | Clause 4.0.4 of T/CECS 1206-2022
90 | Level-1 | To quickly provide sanitary conveniences for infectious patients in the main hall, is it compliant to let them directly use the existing indoor restroom without undergoing any physical retrofitting? | No. Infectious disease patients are strictly prohibited from using any unmodified existing indoor water-use rooms, such as restrooms, shower rooms, or washrooms, within the large-space building. | IfcSpace_R1 | Clause 5.1.3 of T/CECS 1206-2022
91 | Level-1 | When setting up temporary outdoor patient restrooms accessible via the main hall's exterior door, is it acceptable to establish a standard pathway with steps that lacks wheelchair accessibility? | No. A dedicated pathway must be established between the outdoor sanitary facilities and the large-space building, and this pathway is strictly mandated to satisfy barrier-free accessibility requirements. | Connection_ExtDoor_W7 | Clause 5.1.3 of T/CECS 1206-2022
92 | Level-1 | To protect the flooring of the frequently utilized main corridor from heavy foot traffic, is it acceptable to dry-lay standard combustible plastic sheeting to minimize conversion costs? | No. While dry-laid roll materials should be used to protect frequently used floors, safety regulations explicitly mandate that these materials must be flame-retardant or non-combustible; standard combustible plastics are strictly prohibited. | Boundary_Floor_C1 | Clause 5.1.9 of T/CECS 1206-2022
93 | Level-1 | To conserve operational space, can the door connecting the main hall and the storage room be utilized as a bidirectional sanitary passage for both entering and leaving the ward? | No. Entrance and exit sanitary passages to and from the contaminated zone must be strictly separated. Using a single door or pathway for bidirectional movement between zones inherently violates infection control protocols. | Connection_Door_W4 | Clause 5.4.2 of T/CECS 1206-2022
94 | Level-1 | When planning the layout branching off the main corridor, is it compliant to design two sanitary passages for entering the contaminated zone but only provide one sanitary passage for exiting? | No. The decontamination process upon leaving the ward is more complex and time-consuming; therefore, the number of sanitary passages for exiting the contaminated zone must be strictly greater than the number of passages for entering it. | IfcSpace_C1 | Clause 5.4.2 of T/CECS 1206-2022
95 | Level-1 | Can medical staff use the existing interior door connecting the clean corridor directly to the contaminated main hall to save movement time? | No. Direct access between zones of different risk levels is strictly prohibited; a dedicated sanitary passage or buffer room must be established between adjacent areas to maintain the integrity of infection control. | Connection_Door_W13 | Clause 4.0.5 of T/CECS 661-2020
96 | Level-1 | To maximize space utilization, is it permissible to operate the main corridor simultaneously as a clean zone and a semi-contaminated zone without installing any physical partitions? | No. Facilities must be laid out with detailed, distinct functional zoning based on strict diagnostic workflows; mixing clean and semi-contaminated functions within a single unpartitioned space inherently violates this fundamental zoning mandate. | IfcSpace_C1 | Clause 4.0.5 of T/CECS 661-2020
97 | Level-1 | To reduce MEP installation costs, is it permitted to connect the semi-clean main corridor and the contaminated main hall to a single, shared mechanical exhaust system? | No. Mechanical supply and exhaust systems must be established as strictly independent systems based on specific zoning classifications; sharing ventilation ductwork across semi-clean and contaminated zones is explicitly prohibited. | MEP_HVAC_C1_1 | Clause 7.0.1 of T/CECS 661-2020
98 | Level-1 | Is it acceptable for the main hall, functioning as the contaminated patient ward, to be positively pressurized with a higher static air pressure than the adjacent semi-contaminated corridor? | No. To prevent the outbound spread of airborne infectious pathogens, the static air pressure within the contaminated zone must strictly be the lowest in the facility, sequentially decreasing from the semi-contaminated zone down to the contaminated zone. | IfcSpace_M1 | Clause 7.0.1 of T/CECS 661-2020
99 | Level-1 | To streamline ductwork installation, is it permissible to merge the exhaust system of the testing cabin's sample extraction zone with the existing mechanical exhaust ducts of the main corridor? | No. To prevent the spread of infectious agents and cross-contamination, the testing laboratory must never share ductwork with the external environment's general HVAC; it is mandatory to maintain a strictly independent ventilation system. | MEP_HVAC_C1_2 | Clause 5.4.1.4 of T/CIQA 16-2021
100 | Level-1 | If Storage S3 is repurposed as a centralized mechanical room for a custom-built testing cabin, can a single high-power ventilation system be used to simultaneously supply and exhaust air across all protection zones? | No. Utilizing a single shared ventilation system across different functional zones violates laboratory infection control protocols. Distinct protection zones must mandatorily possess their own independent ventilation systems to ensure complete air segregation. | MEP_HVAC_S3 | Clause 5.4.1.4 of T/CIQA 16-2021
101 | Level-2 | During the layout planning, can Storage S1 and its adjacent Outdoor space be safely designated as the medical waste storage and direct pick-up zone? | Yes. Storage S1 provides physical isolation, and its topological connection to the Outdoor space enables the required "direct transport mode without transfer". | IfcSpace_S1, IfcSpace_Outdoor | Clause 7.1.6 of GB/T 45998-202, Clause 7.1.3 of T/CECS 1226-2022
102 | Level-2 | To convert the existing restroom into a patient-use facility, do the current exhaust fan and floor drain meet the baseline standards? | Yes. The floor drain has the required U-shaped water seal, and the independent exhaust fan can provide the strengthened ventilation. | IfcSanitaryTerminal_R1_Drain, IfcAirTerminal_R1_Exhaust | Clause 5.1.2.6 of WS 696-2020, Clause 5.2.3 of WS/T 698-2020
103 | Level-2 | Is the current configuration of the main corridor entrance and the nearby Storage S4 suitable for triage screening and temporary quarantine? | Yes. The entrance door supports the installation of temperature detection devices, and S4 can function as the designated temporary isolation room for suspected cases. | IfcDoor_C1_Entrance, IfcSpace_S4 | Clause 5.1.2 of WS/T 698-2020, Clause 7.1.6 of GB/T 45998-2025
104 | Level-2 | Between the contaminated ward in the main hall and the semi-contaminated main corridor, must their independent mechanical exhaust systems be configured so that the ward's static pressure is strictly lower, and its exhaust vents are placed below 0.3m? | Yes. Regulations mandate independent systems with a pressure gradient sequentially decreasing towards the contaminated zone, and specifically require exhaust vents in the contaminated area to be positioned no higher than 0.3m from the floor. | IfcSpace_M1, IfcSpace_C1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 661-2020
105 | Level-2 | When comparing the HVAC system in the contaminated main hall and the HVAC in the clean locker room, is it legally required that both have strictly independent power supplies that switch to backup generator power within 15 seconds during an outage? | Yes. The power supply for ventilation and air conditioning systems must be independently configured, and medical function areas mandate diesel generators that automatically supply power within 15 seconds of a grid failure. | MEP_HVAC_M1_6, MEP_HVAC_L1 | Clause 8.0.2 of T/CECS 661-2020, Clause 8.0.3 of T/CECS 661-2020
106 | Level-2 | While the main corridor and the main hall operate on independent mechanical ventilation systems, is it explicitly recommended to install an air quality monitoring system specifically in the main hall's bed area? | Yes. Contaminated and semi-contaminated zones must have independent mechanical ventilation, and standards explicitly recommend deploying centralized control and air quality monitoring systems specifically within the patient bed areas. | IfcSpace_C1, IfcSpace_M1 | Clause 9.5.8 of T/CECS 1206-2022, Clause 4.1.5.1 of WS 694-2020
107 | Level-2 | If Storage S4 serves as a buffer room leading into the contaminated main hall, must the airflow organization direct the air strictly from S4 into the main hall while maintaining a pressure differential? | Yes. Buffer rooms must have rational airflow organization measures where the air strictly flows towards the contaminated zone, inherently supporting the requirement that static pressure decreases toward the contaminated area. | IfcSpace_S4, IfcSpace_M1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022
108 | Level-2 | Does the maintenance protocol require the facility team to clean, disinfect, or replace the condensate pans of the HVAC terminals in both the contaminated main hall and the semi-clean locker room every week? | Yes. Regardless of the contamination zoning, all operating air conditioning and ventilation components, specifically including condensate pans and filters, must undergo mandatory cleaning, disinfection, or replacement on a weekly basis. | MEP_HVAC_M1_2, MEP_HVAC_L1 | Clause 5.2.2.4 of WS 696-2020, Clause 5.1.2.5 of WS 696-2020
109 | Level-2 | When inspecting the exhaust outlets of the HVAC in the main hall and the locker room, must both systems have HEPA filters installed that are subjected to weekly cleaning or replacement? | Yes. The exhaust systems in contaminated zones must incorporate coarse, medium, and HEPA filters at the outlets, and maintenance regulations mandate weekly cleaning, disinfection, or replacement of these filters across operating HVAC systems. | MEP_HVAC_M1_4, MEP_HVAC_L1 | Clause 8.2.4 of T/CECS 1206-2022, Clause 5.1.2.5 of WS 696-2020
110 | Level-2 | If Locker Room L1 acts as the "primary changing" exit leading to the clean corridor, is it required to install mechanical ventilation providing at least 40 air changes per hour (ACH) of exhaust from the bottom of the room? | Yes. Infectious disease wards require mechanical ventilation, and specifically, the exit "primary changing" room must have a mechanical exhaust system configured at the lower part of the room delivering no less than 40 ACH. | IfcSpace_L1, IfcSpace_C1 | Clause 8.2.4 of T/CECS 1206-2022, Clause 8.2.1 of T/CECS 1206-2022
111 | Level-2 | When the operation team compiles the basic data profile of the facility's HVAC systems, must they document that the main hall and corridor systems operate on independent power circuits? | Yes. The management protocols require collecting comprehensive HVAC data (types, zones, design parameters), which inherently must reflect the strict regulatory requirement that ventilation power supplies are set up independently. | MEP_HVAC_M1_6, MEP_HVAC_C1_1 | Clause 8.0.3 of T/CECS 661-2020, Clause 6.1.1 of WS 696-2020
112 | Level-2 | Are the independent ventilation systems serving both the main hall and the locker room legally required to be powered by a backup generator that activates within 15 seconds? | Yes. As medical function areas, both zones are mandated to have mechanical ventilation systems whose power supplies are independently configured and supported by a 15-second auto-start diesel generator. | MEP_HVAC_M1_1, MEP_HVAC_L1 | Clause 8.0.2 of T/CECS 661-2020, Clause 8.2.1 of T/CECS 1206-2022
113 | Level-2 | If Locker Room L2 is used as an administrative office area separated from the main hall ward, is it permissible to implement natural ventilation by opening doors in L2 every 2-3 hours? | Yes. For densely populated administrative or office spaces (L2), increasing ventilation by opening doors/windows or using natural ventilation for 20-30 minutes every 2-3 hours is mandated, provided it is fully isolated from the contaminated main hall. | IfcSpace_L2, IfcSpace_M1 | Clause 4.1.5.1 of WS 694-2020, Clause 5.2.2.2 of WS 696-2020
114 | Level-2 | Does the exhaust system in Restroom R1 require the same weekly cleaning of its air outlets and filters as the mechanical exhaust system in the main hall? | Does the exhaust system in Restroom R1 require the same weekly cleaning of its air outlets and filters as the mechanical exhaust system in the main hall? | IfcSpace_R1, IfcSpace_M1 | Clause 4.1.5.1 of WS 694-2020, Clause 5.1.2.5 of WS 696-2020
115 | Level-2 | Must the independent power supplies for the HVAC systems in Storage S3 and S4 be maintained even while their air handling units undergo weekly disinfection? | Yes. The mandate for independent power supplies for ventilation systems is a permanent structural requirement that applies concurrently with the operational requirement for weekly cleaning and disinfection of air handling units. | MEP_HVAC_S3, MEP_HVAC_S4 | Clause 8.0.3 of T/CECS 661-2020, Clause 5.2.2.4 of WS 696-2020
116 | Level-2 | When inspecting the exterior wall W7 of the main hall, must any exhaust vents located there be positioned at the lower part (below 0.3m) and have their filters cleaned weekly? | Yes. In contaminated respiratory zones, exhaust vents must be uniformly distributed at the bottom (not higher than 0.3m), and these components must undergo mandatory weekly cleaning, disinfection, or filter replacement. | MEP_HVAC_M1_3, Boundary_W7 | Clause 8.2.4 of T/CECS 1206-2022, Clause 5.1.2.5 of WS 696-2020
117 | Level-2 | Must the electrical panel supplying the main hall's mechanical exhaust fan (which holds the HEPA filters) be wired to the diesel generator that activates within 15 seconds? | Yes. The exhaust system equipped with HEPA filters is a critical medical ventilation component for the contaminated ward, and its independent power supply must strictly be backed by the 15-second automatic diesel generator. | MEP_HVAC_M1_5, IfcSpace_M1 | Clause 8.0.2 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022
118 | Level-2 | When designing the lab cabin placed in the outdoor area, must it have both an independent ventilation system from the main building and its own independent power supply circuit? | Yes. Testing cabins require completely independent ventilation to prevent airborne cross-contamination, and all medical ventilation and air conditioning systems are universally mandated to have independently configured power supplies. | IfcSpace_Outdoor, IfcSpace_M1 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.0.3 of T/CECS 661-2020
119 | Level-2 | During decommissioning, must the patient chairs in the main hall be removed before dismantling the HVAC pipes, and can those metal and PVC HVAC pipes be categorized as recyclable materials? | Yes. The dismantling sequence mandates removing furniture before MEP facilities. Additionally, materials like PVC panels, cable trays, and ventilation/plumbing pipes are strictly classified as recyclable dismantled materials. | Equipment_Chair_2, MEP_HVAC_M1_1 | Clause 6.1.4 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022
120 | Level-2 | Before clearing out the epidemic-related waste, such as used masks and gloves left near the patient beds in the main hall, must the air and surfaces undergo terminal disinfection and pass evaluation? | Yes. Terminal disinfection of the air, surfaces, and bed units must be completed and evaluated as qualified before any leftover epidemic-related waste or other materials can be transported out of the cabin. | IfcSpace_M1, Equipment_Bed_M1 | Clause 5.1.2 of T/CECS 1226-2022, Clause 4.1.4 of T/CECS 1226-2022
121 | Level-2 | When decommissioning and restoring the facility, must the HVAC in the corridor and lighting in the hall undergo terminal disinfection before dismantling, and be commissioned to a qualified state after restoration? | Yes. Terminal disinfection must pass evaluation prior to dismantling any regional equipment. Furthermore, during the restoration phase, MEP facilities (including HVAC and electrical systems) must be fully recommissioned to a qualified status. | MEP_HVAC_C1_1, MEP_Light_M1_1 | Clause 5.1.3 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
122 | Level-2 | If fluorescent tubes are removed from the main hall's lighting fixtures, must they be classified as hazardous waste, and must their final disposal site in the outdoor transport process be recorded in the ledger? | If fluorescent tubes are removed from the main hall's lighting fixtures, must they be classified as hazardous waste, and must their final disposal site in the outdoor transport process be recorded in the ledger? | MEP_Light_M1_2, IfcSpace_Outdoor | Clause 4.1.6 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
123 | Level-2 | Must the overall decommissioning plan compiled before the project begins explicitly include a scheme for restoring existing building components like the main hall's floors and exterior windows? | Yes. An overall decommissioning plan is required before implementation, and it must explicitly include schemes for restoring existing buildings and sites, which covers surface finishes, floors, doors, and glass windows. | Boundary_Floor_M1, Connection_ExtWin_W25 | Clause 3.0.2 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022
124 | Level-2 | When removing the restroom plumbing fixtures (Step 2 of dismantling), must any wastewater generated be pre-treated by the shelter's on-site systems before being discharged into the outdoor municipal sewage network? | Yes. MEP and plumbing equipment must be removed following furniture removal, and any wastewater generated during this dismantling process must utilize existing treatment facilities for pre-treatment before municipal discharge. | Equipment_Toilet_3, IfcSpace_Outdoor | Clause 6.1.4 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022
125 | Level-2 | Are the abandoned bedding and daily necessities found near the beds in the main hall classified as "other dismantled items," and must their removal wait until the space's terminal disinfection is deemed qualified? | Yes. Leftover bedding and daily necessities are defined as "other dismantled items." They can only be safely removed from the cabin after the terminal disinfection of the air and object surfaces has been successfully evaluated. | Equipment_Bed_M1, IfcSpace_M1 | Clause 4.1.5 of T/CECS 1226-2022, Clause 5.1.2 of T/CECS 1226-2022
126 | Level-2 | Can the temporary PVC bed partitions be sorted as recyclable materials, and must the original existing doors and connecting walls be fully restored to their pre-pandemic condition? | Yes. PVC panels and bed partitions are legally defined as recyclable dismantled materials. Furthermore, the restoration of the existing building fundamentally mandates the recovery of its original walls and doors. | Boundary_W55, Connection_Door_W6 | Clause 4.1.3 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022
127 | Level-2 | Should the overall decommissioning plan estimate the investment needed for the fire extinguishers and HVAC systems, and must these systems be tested and verified as qualified after being restored? | Yes. The overall implementation scheme must include engineering investment plans covering MEP systems. Upon restoration, facilities like HVAC and fire protection must be rigorously commissioned until they are verified as qualified. | MEP_HVAC_M1_5, Equipment_FireExtinguisher_C1 | Clause 3.0.2 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
128 | Level-2 | Must the storage cabinets be dismantled before the HVAC terminals, and should the waste filter cartridges removed from those HVAC units be classified strictly as hazardous waste? | Yes. The mandated sequence requires furniture (cabinets) to be removed before MEP equipment (HVAC). Additionally, used filter cartridges and activated carbon from ventilation systems are explicitly categorized as hazardous waste. | Equipment_Cabinet_A_S4, MEP_HVAC_M1_4 | Clause 6.1.4 of T/CECS 1226-2022, Clause 4.1.6 of T/CECS 1226-2022
129 | Level-2 | Must the original floor drains in the main hall be completely sealed before using the space, and is it prohibited to install new floor drains since the hall is a non-flushing dry floor area? | Yes. Construction rules mandate that all original floor drains and drainage ditches must be sealed before use. Furthermore, for floors without washing/flushing requirements, installing new floor drains is strictly prohibited. | Boundary_Floor_M1, Equipment_FloorDrain_M1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 4.3.9 of T/CADBM 72-2023
130 | Level-2 | For the HVAC units in the contaminated main hall, must their condensate water drain indirectly into the sewage pipes, and must their U-traps be checked weekly for water depletion? | Yes. Air conditioning condensate in contaminated zones must be indirectly discharged into the sewage system. Additionally, operations protocols require weekly inspections of the U-traps for HVAC condensate drains to ensure the water seal is intact. | MEP_HVAC_M1_2, MEP_Drainage_M1 | Clause 4.3.4 of T/CADBM 72-2023, Clause 5.1.2.6 of WS 696-2020
131 | Level-2 | Must the exhaust vent pipe from the main hall's drainage system be positioned at least 4.0m away from any fresh air intakes, and must its exit be equipped with a HEPA filter or disinfection device? | Yes. Drainage vent pipes must maintain a minimum 4.0m distance from fresh air intakes. Because the main hall serves as an isolation zone, its vent exits are strictly required to be fitted with HEPA filters or disinfection devices. | MEP_VentPipe_M1, MEP_FreshAir_M1_1 | Clause 7.4.3 of T/CECS 1206-2022, Clause 6.0.7 of T/CECS 661-2020
132 | Level-2 | During the installation of drainage pipes in Restroom R1 and Corridor C1, must the contractors perform closed-water tests and implement strict anti-leakage measures for both areas? | Yes. Multiple facility standards universally mandate that all drainage pipelines must undergo rigorous closed-water tests and incorporate reliable measures (like hot-melt connections) to prevent sewage leakage and outward seepage. | MEP_Drainage_R1, MEP_Drainage_C1 | Clause 4.3.6 of T/CADBM 72-2023, Clause 6.0.8 of T/CECS 661-2020
133 | Level-2 | If Restroom R1 is a containerized cabin deployed outdoors, must it undergo a water spray test for leak-proofing, and must its outdoor sewage pipes remain strictly separated from the outdoor rainwater drains? | Yes. Container cabins require anti-leakage measures and water spray tests upon installation. Furthermore, the outdoor rainwater and sewage/wastewater drainage networks must adopt a separated flow system and strictly forbid cross-connections. | IfcSpace_Outdoor, IfcSpace_R1 | Clause 3.2.12 of T/CADBM 72-2023, Clause 4.3.1 of T/CADBM 72-2023
134 | Level-2 | Inside Restroom R1, should the water supply and drainage pipes be surface-mounted, and if routed parallel to each other, must they maintain an indoor horizontal clearance of at least 0.5 meters? | Yes. Indoor water supply and drainage pipelines are advised to be surface-mounted. When laid parallel indoors, the minimum horizontal clearance between the water supply pipe and the drainage pipe must not be less than 0.5m. | MEP_Supply_R1, MEP_Drainage_R1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 5.2.9 of T/CADBM 72-2023
135 | Level-2 | Must the vent pipe serving Restroom R1 be made of the same material as its plastic drainage pipe, and must its exhaust be discharged at a high altitude away from human activity areas? | Yes. The vent pipe material is recommended to match the drainage pipe material. Moreover, the exhaust from the sewage vent must be discharged at a high altitude and kept away from any zones with human activity. | MEP_VentPipe_R1, MEP_Drainage_R1 | Clause 3.3.3 of T/CADBM 72-2023, Clause 4.3.13 of T/CADBM 72-2023
136 | Level-2 | In the public Restroom R1 where the floor requires flushing, must it be fitted with non-water-seal floor drains with P-traps, and must the ends of its horizontal drainage pipes be equipped with cleanouts? | Yes. Floors requiring flushing must install floor drains (specifically filter-equipped non-water-seal drains combined with traps). Additionally, cleanouts are mandatory at the end terminals of all horizontal drainage pipes in public restrooms. | MEP_Drainage_R1, Equipment_FloorDrain_R1 | Clause 4.3.9 of T/CADBM 72-2023, Clause 5.3.6 of T/CADBM 72-2023
137 | Level-2 | After the facility is decommissioned, if the temporary drainage pipes in the main hall are retained instead of dismantled, must their ends be securely sealed, just as the original floor drains were sealed prior to operation? | Yes. Before operation, original floor drains must be sealed. During decommissioning, if any temporary drainage systems or pipes are evaluated and chosen to be retained rather than dismantled, they must be securely sealed off. | MEP_Drainage_M1, Boundary_Floor_M1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 13.2.2 of T/CECS 1206-2022
138 | Level-2 | If Restroom R1 is a container cabin where a septic tank cannot be installed due to space constraints, must its internal sanitary fixtures be placed against the exterior wall, and its shower wastewater collected via sealed pipes for disinfection? | Yes. Internal sanitary facilities in container cabins must be adjacent to the exterior walls. If a septic tank is unfeasible, shower wastewater can bypass it by being independently collected via airtight pipes and discharged after disinfection. | Equipment_Shower_R1, IfcSpace_R1 | Clause 3.2.12 of T/CADBM 72-2023, Clause 4.3.1 of T/CADBM 72-2023
139 | Level-2 | Must the patient beds in the main hall be spaced at least 1.2m apart, and should each bed's headboard be equipped with three 220V combo sockets? | Yes. Regulations strictly mandate that the distance between patient beds must be greater than 1.2m. Additionally, each bed head should be equipped with three 220V/10A combo sockets, one of which should feature a USB port. | Equipment_Bed_M1, MEP_Power_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 9.5.6 of T/CECS 1206-2022
140 | Level-2 | If the peacetime lighting in the main hall causes glare to patients, must separate overhead lighting be installed away from the direct top of the beds, and should each bed also have a dedicated bedside lamp? | Yes. Ward lighting must not cause glare; if peacetime lighting fails this, it must be separately re-installed avoiding the space directly above beds. Furthermore, each bed is explicitly required to have a bedside lamp or a desk lamp. | MEP_Light_M1_1, Equipment_Bed_M1 | Clause 9.7.3 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
141 | Level-2 | Must every bed in the contaminated ward be equipped with at least 2 medical oxygen terminals, and must the facility's total oxygen design flow be calculated assuming 100% simultaneous usage? | Yes. Medical gas standards for emergency facilities dictate that each bed should have 2 oxygen terminals (along with vacuum and medical air), and the oxygen design flow must safely account for a 100% simultaneous usage rate across all beds. | Equipment_Bed_M1, MEP_Gas_M1 | Clause 9.0.3 of T/CECS 661-2020, Clause 9.0.4 of T/CECS 661-2020
142 | Level-2 | When partitioning the main hall, must each zone be capped at 50 beds, and should a centralized drinking water point be established for each nursing unit based on its bed count? | Yes. Bed zones must be separated by gender and capped at a maximum of 50 beds per zone. Concurrently, drinking water points (boilers or bottled dispensers) must be reasonably distributed by nursing unit capacity. | IfcSpace_M1, Equipment_WaterDispenser_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 7.3.6 of T/CECS 1206-2022
143 | Level-2 | Can the required bedside illumination for a patient be achieved simply by plugging a desk lamp into one of the three 220V sockets installed at the bedside table? | Yes. The standards explicitly permit providing bedside illumination either through fixed bedhead lights or by utilizing a desk lamp plugged into the bedside cabinet's mandated 220V socket configuration. | MEP_Power_M1, MEP_Light_M1_2 | Clause 9.5.6 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
144 | Level-2 | During the initial assessment of the main hall, must the evaluation guarantee that the conversion won't impact its normal peacetime use, while strictly partitioning the beds by gender? | Yes. Converting large-space buildings mandates a pre-assessment to ensure high utilization without compromising the building's peacetime functions. In operation, the layout must strictly enforce bed zoning and gender separation. | IfcSpace_M1, Equipment_Bed_M1 | Clause 3.0.1 of T/CECS 1206-2022, Clause 4.1.3.4 of WS 694-2020
145 | Level-2 | Should the public areas within the ward provide electrical sockets for cleaning and smart devices, while the individual beds are equipped with their own trash cans and storage boxes? | Yes. Public areas should be fitted with sockets dedicated to cleaning and smart equipment. Simultaneously, each individual bed unit must be provisioned with personal necessities, specifically including a storage box and a trash can. | MEP_Power_M1, Equipment_Bed_M1 | Clause 9.5.6 of T/CECS 1206-2022, Clause 4.1.3.4 of WS 694-2020
146 | Level-2 | Must the new overhead lighting in the ward incorporate anti-glare measures, and must the facility's medical air and vacuum terminals be provided at no less than 1 per bed? | Yes. Ward lighting must proactively adopt anti-glare measures to protect patients lying on their backs. Regarding medical gases, while oxygen requires 2 terminals, medical vacuum and medical air must be provided at no less than 1 terminal per bed. | MEP_Light_M1_1, MEP_Gas_M1 | Clause 9.7.3 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020
147 | Level-2 | Must the electrical loads in the main hall and corridor be graded based on reliability needs, and should their power circuits be established independently from peacetime commercial loads? | Yes. Electrical loads must be graded according to reliability requirements, safety, and economic impact. Furthermore, the power supply circuits for the emergency shelter must be independently configured and separated from peacetime loads. | MEP_Power_M1, MEP_Power_C1 | Clause 9.2.1 of T/CECS 1206-2022, Clause 9.3.3 of T/CECS 1206-2022
148 | Level-2 | Must the exterior wall facing the outdoor plaza reserve cable sleeves, and should the outdoor diesel generator feed its power into the facility's total electrical distribution room? | Yes. Large space exterior walls facing outdoor plazas must explicitly reserve wall-penetrating cable sleeves. Both the municipal grid and the outdoor emergency generator must feed their power into the main distribution room for central routing. | Boundary_W7, MEP_ElecRoom | Clause 9.6.3 of T/CECS 1206-2022, Clause 9.5.1 of T/CECS 1206-2022
149 | Level-2 | If the peacetime electrical system cannot meet the main hall's load, is it compliant to supplement it with an outdoor box-type diesel generator that automatically starts during blackouts? | Yes. When the peacetime power system is insufficient, supplementing it with a box-type diesel generator is explicitly permitted. This emergency generator must feature an automatic start mechanism that restores power upon grid failure. | IfcSpace_M1, MEP_Generator_Outdoor | Clause 9.3.2 of T/CECS 1206-2022, Clause 9.4.2 of T/CECS 1206-2022
150 | Level-2 | Must the facility guarantee 24-hour uninterrupted power to the main hall, utilizing dual power supplies or emergency setups to restore key areas within 30 minutes of a sudden blackout? | Yes. Emergency medical facilities must maintain 24h uninterrupted power and are recommended to use dual power supplies. In sudden blackout events, emergency power restoration for critical areas must strictly be completed within 30 minutes. | IfcSpace_M1, MEP_Power_Main | Clause 12.0.9 of T/CECS 1206-2022, Clause 9.3.1 of T/CECS 1206-2022
151 | Level-2 | If a containerized nucleic acid lab is deployed inside the main hall, is it permitted to link its ventilation ductwork with the main corridor's HVAC to share the 15-second backup diesel generator? | No. While medical ventilation requires a 15-second backup generator, the testing cabin's ventilation system must be set up completely independently from any other work areas to prevent cross-contamination. | IfcSpace_M1, MEP_HVAC_C1_1 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.0.2 of T/CECS 661-2020
152 | Level-2 | Can the contaminated main hall maintain its required negative pressure gradient relative to the clean locker room simply by keeping the connecting doors open for natural draft instead of installing mechanical systems? | No. Infectious disease wards must explicitly install mechanical ventilation systems; relying on natural draft through open doors violates both the mechanical ventilation mandate and the strict air pressure control requirements. | IfcSpace_M1, IfcSpace_L1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.1 of T/CECS 1206-2022
153 | Level-2 | To increase fresh air frequency in the densely populated main hall ward, is it compliant to temporarily open its exterior windows for 30 minutes every 2 hours, as long as the mechanical ventilation is running? | No. Although office spaces encourage opening windows, the main hall acts as a contaminated ward where opening windows would destroy the required negative static pressure gradient, causing infectious aerosols to leak outward. | IfcSpace_M1, Connection_ExtWin_W25 | Clause 7.0.1 of T/CECS 661-2020, Clause 5.2.2.2 of WS 696-2020
154 | Level-2 | Can the HVAC terminal in the main hall share its electrical control circuit with the ambient lighting fixtures to simplify the interlocking and fault alarm functions at the central control box? | No. The power supply for ventilation systems must be established independently from lighting and other loads, even though the control box itself must realize interlocking and fault alarm functions. | MEP_HVAC_M1_1, MEP_Light_M1_1 | Clause 8.0.3 of T/CECS 661-2020, Clause 9.5.8 of T/CECS 1206-2022
155 | Level-2 | If the grid power fails, is it acceptable for the main hall's HVAC to remain off for 5 minutes while the corridor's HVAC continues running, as long as the main hall's pressure eventually drops lower? | No. Maintaining the pressure gradient is continuous; the diesel generator must automatically start and restore power to the medical ventilation systems in all zones within a strict 15-second window during a power interruption. | MEP_HVAC_C1_1, MEP_HVAC_M1_3 | Clause 8.0.2 of T/CECS 661-2020, Clause 7.0.1 of T/CECS 661-2020
156 | Level-2 | Is it compliant to configure the independent mechanical ventilation in the main hall ward such that the fresh air volume exactly equals the exhaust air volume (both at 150m³/h per person) to balance the airflow with the corridor? | No. While zones must be independent, the fresh air volume in a contaminated respiratory ward must not exceed 80% of the exhaust air volume to safely maintain the required negative pressure differential against adjacent spaces. | IfcSpace_M1, IfcSpace_C1 | Clause 8.2.4 of T/CECS 1206-2022, Clause 4.1.5.1 of WS 694-2020
157 | Level-2 | If a containerized lab is placed in the outdoor area, can it utilize the exhaust fans of the main hall to ensure its internal air pressure is lower than the outdoor atmospheric pressure? | No. The ventilation system of a nucleic acid testing cabin must be established entirely independently; it cannot share exhaust fans with the main hospital building, even if aiming to achieve pressure controls. | IfcSpace_Outdoor, IfcSpace_M1 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 7.0.1 of T/CECS 661-2020
158 | Level-2 | Can the independent mechanical exhaust system in the contaminated main hall operate without a standby backup fan if the adjacent corridor's HVAC has dual fans? | No. The systems must be strictly independent by zone, and the regulations explicitly dictate that the exhaust fan units for the contaminated zone (main hall) should be equipped with their own dedicated standby backup units and interlocking motorized airtight valves. | MEP_HVAC_M1_5, MEP_HVAC_C1_2 | Clause 8.2.4 of T/CECS 1206-2022, Clause 4.1.5.1 of WS 694-2020
159 | Level-2 | If Storage S2 serves as a buffer room between the semi-clean corridor and the contaminated ward, can the static air pressure in S2 be kept strictly higher than the corridor? | No. The static air pressure must sequentially decrease from the semi-clean zone (corridor) through the semi-contaminated zone (buffer S2) down to the contaminated zone; thus, S2's pressure must be lower than the corridor's. | IfcSpace_S2, IfcSpace_C1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022
160 | Level-2 | For a container lab installed inside the main hall, can its ventilation interlocking controls be merged with the main hall's HVAC control box to save electrical panel space? | No. The testing cabin's ventilation must be completely independent from other work areas, and combining their control boxes violates the independence rule, despite the general requirement for centralized interlocking alarms. | IfcSpace_M1, MEP_HVAC_M1_2 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 9.5.8 of T/CECS 1206-2022
161 | Level-2 | When traversing the door between the contaminated main hall and the buffer room S2, should the airflow be organized to move from the main hall into S2 to maintain the pressure gradient? | No. To prevent pathogen escape, the static pressure must be lower in the contaminated zone; therefore, airflow organization must strictly direct air from the buffer room (S2) into the contaminated zone (main hall), not the reverse. | Connection_Door_W4, IfcSpace_M1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022
162 | Level-2 | If the main hall's ventilation fails during a power outage because the 15-second generator malfunctions, is it an acceptable backup strategy to immediately open the exterior windows to ventilate the ward? | No. Relying on natural ventilation via windows in a contaminated ward is strictly prohibited as it destroys infection control gradients; the facility must rely on the mandated mechanical ventilation backed by a functional 15-second generator. | IfcSpace_M1, Connection_ExtWin_W25 | Clause 8.0.2 of T/CECS 661-2020, Clause 5.2.2.2 of WS 696-2020
163 | Level-2 | Even if the main hall's fresh air system is configured to supply 90% of the exhaust air volume, is the setup compliant if the main corridor's HVAC has centralized interlocking controls? | No. Centralized interlocking controls cannot override fundamental airflow safety limits; the fresh air volume in the contaminated respiratory ward must strictly not exceed 80% of the exhaust volume to maintain negative pressure. | IfcSpace_M1, MEP_HVAC_C1_1 | Clause 9.5.8 of T/CECS 1206-2022, Clause 8.2.4 of T/CECS 1206-2022
164 | Level-2 | Is it legally compliant to skip installing mechanical ventilation in the contaminated Storage S5 as long as the adjacent clean Locker Room L1 has a powerful positive pressure HVAC system? | No. Every space serving as an infectious disease or radiation ward/zone must explicitly have its own mechanical ventilation installed; relying solely on the positive pressure spillover from an adjacent clean zone is a severe violation. | IfcSpace_S5, IfcSpace_L1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.1 of T/CECS 1206-2022
165 | Level-2 | If the corridor's HVAC receives weekly cleaning but the main hall's independent exhaust system was installed without a standby backup fan unit, does the facility pass the safety inspection? | No. Weekly maintenance of one zone does not negate structural flaws in another; the exhaust fan units in the contaminated zone (main hall) are explicitly required to be equipped with standby units to prevent catastrophic failure. | MEP_HVAC_C1_2, MEP_HVAC_M1_4 | Clause 8.2.4 of T/CECS 1206-2022, Clause 5.2.2.4 of WS 696-2020
166 | Level-2 | Can the demolition team tear down the temporary partition walls before removing the washroom sinks, and discharge the resulting wastewater directly into the outdoor municipal pipes without pre-treatment? | No. Partitions (Step 3) must be removed after plumbing fixtures (Step 2). Furthermore, wastewater generated during this process must be pre-treated using the shelter's existing facilities before any outdoor municipal discharge. | Boundary_W55, Equipment_Sink_3 | Clause 6.1.4 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022
167 | Level-2 | To speed up the decommissioning of the main hall, is it permitted to immediately clear out epidemic-related waste like used gloves before the terminal disinfection of the bed units is evaluated and approved? | No. Epidemic-related waste (like used gloves) must not be cleared out immediately; terminal disinfection of the space and bed units must be conducted and formally evaluated as qualified before any waste removal occurs. | IfcSpace_M1, Equipment_Bed_M1 | Clause 5.1.2 of T/CECS 1226-2022, Clause 4.1.4 of T/CECS 1226-2022
168 | Level-2 | Can the fluorescent tubes from the corridor's lighting fixtures be mixed and recycled along with the dismantled aluminum window frames as standard recyclable materials? | No. While window frames are standard recyclable materials, fluorescent tubes are explicitly categorized as hazardous waste. Mixing them violates safety protocols and hazardous waste handling regulations. | MEP_Light_C1_1, Connection_ExtWin_W25 | Clause 4.1.6 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022
169 | Level-2 | When restoring the facility, is it compliant to physically reinstall the main hall's electrical lighting without commissioning it, while completely skipping the cosmetic restoration of the corridor floor? | No. Restoration rules strictly mandate that existing floors must be comprehensively restored, and electrical/MEP systems must not only be reinstalled but also commissioned to a qualified operational status. | Boundary_Floor_C1, MEP_Light_M1_1 | Clause 6.3.2 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
170 | Level-2 | Since the main hall is a temporary emergency structure, can the demolition proceed without drafting an overall scheme and without logging the waste transport vehicles in an outdoor ledger? | No. An overall decommissioning scheme must be compiled before any dismantling begins. Furthermore, a strict ledger recording all waste transport volumes, vehicle information, and final disposal sites must be maintained. | IfcSpace_M1, IfcSpace_Outdoor | Clause 3.0.2 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
171 | Level-2 | Can the table and chair sets in the locker room be removed before the room's terminal disinfection is evaluated as qualified, and should the HVAC be dismantled prior to these furniture items? | No. Terminal disinfection must pass evaluation before dismantling begins. Moreover, the dismantling sequence strictly dictates that furniture (tables/chairs) must be removed before any MEP systems like HVAC. | MEP_HVAC_M1_6, Equipment_TableChairSet_L2 | Clause 5.1.3 of T/CECS 1226-2022, Clause 6.1.4 of T/CECS 1226-2022
172 | Level-2 | Should the abandoned bedding from the patient wards and the daily necessities left in the staff storage be classified as highly infectious epidemic waste, just like used surgical masks? | No. Used surgical masks are classified as epidemic-related waste. However, leftover bedding and daily necessities are legally classified separately under "other dismantled items," requiring different management protocols. | Equipment_Bed_M1, IfcSpace_S2 | Clause 4.1.4 of T/CECS 1226-2022, Clause 4.1.5 of T/CECS 1226-2022
173 | Level-2 | Can hazardous waste, such as the used activated carbon extracted from the main hall's HVAC filters, be transported to an outdoor facility without recording its final disposal site in the official ledger? | No. Used activated carbon is explicitly classified as hazardous waste. Its entire lifecycle, crucially including the final disposal and consumption site, must be accurately documented in the full-process ledger. | MEP_HVAC_M1_4, IfcSpace_Outdoor | Clause 4.1.6 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
174 | Level-2 | To minimize restoration costs, is it permitted to leave the damaged interior doors unrestored, and can the wastewater from removing the toilets be discharged directly into the municipal network? | No. The existing building's restoration strictly mandates the recovery of doors and windows. Furthermore, wastewater generated from dismantling toilets must be pre-treated on-site before municipal discharge. | Connection_Door_W6, Equipment_Toilet_4 | Clause 6.3.2 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022
175 | Level-2 | Can a simple visual inspection of the main hall replace the formal evaluation of terminal disinfection before the corridor's HVAC systems and medical equipment are dismantled and removed? | No. Visual inspection is insufficient and legally invalid. Both the clearance of leftover items and the physical dismantling of equipment must only occur after the formal terminal disinfection effect evaluation is certified as qualified. | IfcSpace_M1, MEP_HVAC_C1_1 | Clause 5.1.2 of T/CECS 1226-2022, Clause 5.1.3 of T/CECS 1226-2022
176 | Level-2 | Can the original floor drains in the non-flushing main hall be kept unsealed and utilized to regularly wash the ward floors to maintain hygiene during the facility's operation? | No. Original floor drains must be strictly sealed before the facility operates. Additionally, for indoor areas like the main hall that lack designed flushing drainage systems, the installation or use of floor drains is strictly prohibited. | Boundary_Floor_M1, Equipment_FloorDrain_M1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 4.3.9 of T/CADBM 72-2023
177 | Level-2 | To avoid the maintenance burden of checking U-traps weekly, can the HVAC condensate pan in the contaminated main hall be hard-piped to drain directly into the sewage pipe without an indirect air gap? | No. Direct drainage is prohibited for safety reasons; condensate from contaminated zones must be indirectly discharged into the sewage pipe. Furthermore, the weekly inspection of the U-trap water seal cannot be bypassed. | MEP_HVAC_M1_2, MEP_Drainage_M1 | Clause 4.3.4 of T/CADBM 72-2023, Clause 5.1.2.6 of WS 696-2020
178 | Level-2 | For aesthetic purposes, can the water supply and drainage pipes in Corridor C1 be concealed within the walls, and can the supply pipe be placed underneath the drainage pipe without any protective casing? | No. Indoor plumbing in emergency facilities should be surface-mounted, not concealed. If a water supply pipe must cross underneath a drainage pipe, it is strictly required to be enclosed in a protective casing at least 3 times the drainage pipe's diameter. | MEP_Supply_C1, MEP_Drainage_C1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 5.2.9 of T/CADBM 72-2023
179 | Level-2 | Is it permissible to merge the outdoor rainwater and contaminated sewage lines into a single combined sewer network, and exhaust the sewage vent pipes at ground level to simplify construction? | No. Outdoor rainwater and sewage networks must be strictly separated; cross-connections are forbidden. Furthermore, sewage vent pipes must discharge at a high altitude and cannot be placed near ground-level human activity areas. | IfcSpace_Outdoor, MEP_VentPipe_M1 | Clause 4.3.1 of T/CADBM 72-2023, Clause 4.3.13 of T/CADBM 72-2023
180 | Level-2 | Can the drainage vent pipe for Corridor C1 use standard carbon steel while the drainage pipe uses PVC, and can its roof exit be placed only 1 meter away from the main hall's fresh air intake? | Can the drainage vent pipe for Corridor C1 use standard carbon steel while the drainage pipe uses PVC, and can its roof exit be placed only 1 meter away from the main hall's fresh air intake? | MEP_VentPipe_C1, MEP_FreshAir_M1_1 | Clause 3.3.3 of T/CADBM 72-2023, Clause 7.4.3 of T/CECS 1206-2022
181 | Level-2 | In the public Restroom R1, is it acceptable to omit the cleanouts at the ends of the horizontal sewage pipes, and to leave the isolation zone's vent pipe exits fully open without HEPA filters? | No. Cleanouts are explicitly required at the ends of horizontal drainage pipes in public restrooms. Additionally, the vent pipe exits for isolation zones must be equipped with HEPA filters or sterilization devices to prevent airborne transmission. | MEP_Drainage_R1, MEP_VentPipe_R1 | Clause 5.3.6 of T/CADBM 72-2023, Clause 6.0.7 of T/CECS 661-2020
182 | Level-2 | Can the main hall's drainage pipelines skip the mandatory closed-water test to accelerate the construction schedule, as long as high-quality flexible cast iron pipes are utilized? | No. The use of high-quality materials does not exempt the system from safety testing. Closed-water tests and anti-leakage measures are strict, non-negotiable mandates for all drainage piping systems in emergency medical facilities. | MEP_Drainage_M1, IfcSpace_M1 | Clause 4.3.6 of T/CADBM 72-2023, Clause 6.0.8 of T/CECS 661-2020
183 | Level-2 | In a containerized locker room L1, can the newly added toilets be placed centrally far from the exterior walls, and can the vertical sewage stack skip the installation of an inspection port at the lowest floor? | No. When sanitary facilities are installed in container units, they should adjoin the exterior walls. Moreover, for sewage vertical stacks, an inspection port is absolutely required at the lowest floor and the highest floor with sanitary fixtures. | IfcSpace_L1, Equipment_Toilet_L1 | Clause 3.2.12 of T/CADBM 72-2023, Clause 5.3.6 of T/CADBM 72-2023
184 | Level-2 | In the outdoor area, can the water supply pipeline and the combined rainwater-sewage pipeline be laid out parallel to each other with only a 0.2-meter horizontal clearance? | No. Firstly, outdoor rainwater and sewage must be separate systems (not combined). Secondly, when outdoor water supply and drainage pipes are laid parallel, the horizontal net clearance between them must not be less than 1.0 meter. | IfcSpace_Outdoor, MEP_Supply_Outdoor | Clause 4.3.1 of T/CADBM 72-2023, Clause 5.2.9 of T/CADBM 72-2023
185 | Level-2 | When decommissioning Restroom R1, if the temporary drainage pipes are not dismantled, can they be left unsealed, under the assumption that their floor drain U-traps were thoroughly checked every week during operation? | No. Routine maintenance (like weekly U-trap checks) during operation does not negate decommissioning safety protocols. Any temporary drainage pipes that are assessed and determined to remain in place must be strictly sealed off. | Equipment_FloorDrain_R1, MEP_Drainage_R1 | Clause 5.1.2.6 of WS 696-2020, Clause 13.2.2 of T/CECS 1206-2022
186 | Level-2 | To fit more patients into the main hall, is it permitted to reduce the bed spacing to 1.0m, provided each bed is upgraded with 3 medical oxygen terminals instead of 2? | No. Upgrading gas terminals does not override fundamental spatial distancing rules. The spacing between beds must remain greater than 1.2m at all times to prevent cross-infection, regardless of the medical equipment provided. | Equipment_Bed_M1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 9.0.3 of T/CECS 661-2020
187 | Level-2 | Is it compliant to install high-intensity overhead lighting directly above the beds to assist doctors, while only providing one 220V power socket per bed to save electrical capacity? | No. High-intensity lighting directly above beds is strictly forbidden as it causes severe glare for patients. Furthermore, beds are recommended to have three 220V combo sockets (including USB), not just one. | MEP_Light_M1_1, MEP_Power_M1 | Clause 9.7.3 of T/CECS 1206-2022, Clause 9.5.6 of T/CECS 1206-2022
188 | Level-2 | To reduce infrastructure costs, can the oxygen design flow be calculated at a 50% simultaneous use rate, and drinking water be limited to one centralized dispenser for a 200-bed zone? | No. Medical oxygen flow must be robustly calculated at a 100% simultaneous usage rate. Additionally, bed zones must not exceed 50 beds, and water points must be reasonably distributed by nursing units, not sparse. | MEP_Gas_M1, Equipment_WaterDispenser_M1 | Clause 9.0.4 of T/CECS 661-2020, Clause 7.3.6 of T/CECS 1206-2022
189 | Level-2 | Can the emergency conversion permanently alter the main hall's structural columns to maximize capacity, and can patients be grouped into zones of 80 beds? | No. The conversion must absolutely not affect the building's normal peacetime use, meaning permanent structural alterations are prohibited. Additionally, the maximum capacity for any single partitioned bed zone is strictly capped at 50 beds. | IfcSpace_M1, Equipment_Bed_M1 | Clause 3.0.1 of T/CECS 1206-2022, Clause 4.1.3.4 of WS 694-2020
190 | Level-2 | Is it acceptable to omit bedside sockets to save wiring, requiring patients to use public corridor sockets for their bedside desk lamps? | No. Bedside electrical sockets are mandatory; each bed should have three combo sockets at the headboard. Relying on public corridor sockets for personal bedside lamps is non-compliant and creates safety and usability hazards. | MEP_Power_C1, Equipment_Bed_M1 | Clause 9.5.6 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
191 | Level-2 | Can two adjacent beds share a single medical oxygen terminal if they are spaced 1.5m apart and each patient is provided with a bedside table and bedding? | No. While the 1.5m spacing and provision of personal bedside tables are compliant, sharing medical gases is prohibited. The standard explicitly requires that every individual bed possesses its own 2 oxygen terminals. | MEP_Gas_M1, Equipment_Bed_M1 | Clause 9.0.3 of T/CECS 661-2020, Clause 4.1.3.4 of WS 694-2020
192 | Level-2 | If the peacetime lighting causes glare to patients, can the facility skip retrofitting the overhead lighting and just rely entirely on individual bedside desk lamps for the ward's illumination? | No. Bedside lamps are for localized illumination. If the main overhead lighting causes glare or fails requirements, the standard dictates it must be separately redesigned and reinstalled with anti-glare measures; it cannot simply be abandoned. | MEP_Light_M1_1, MEP_Light_M1_2 | Clause 9.7.3 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
193 | Level-2 | Can the facility calculate oxygen supply at an 80% usage capacity if it guarantees every bed receives four combo power sockets instead of the mandated three? | No. Increasing the number of power sockets does not permit a compromise on life-saving medical gases. The oxygen design flow must be rigorously calculated at 100% simultaneous usage across all beds, regardless of electrical upgrades. | MEP_Gas_M1, MEP_Power_M1 | Clause 9.0.4 of T/CECS 661-2020, Clause 9.5.6 of T/CECS 1206-2022
194 | Level-2 | Can the main hall share a non-exclusive power circuit with a peacetime commercial mall, and use a manual-start diesel generator that restores the ward's HVAC in 20 seconds? | No. If circuits are shared, they must be dedicated exclusively to the shelter during epidemics. Furthermore, the diesel generator powering the medical HVAC must auto-start (not manual) and restore power within 15 seconds, not 20 seconds. | MEP_Power_M1, MEP_HVAC_M1 | Clause 9.3.3 of T/CECS 1206-2022, Clause 8.0.2 of T/CECS 661-2020
195 | Level-2 | Is it compliant to rely solely on the 15-second generator for the main hall's PCR testing equipment without a UPS, while failing to reserve cable sleeves in the exterior wall? | No. PCR testing equipment requires power restoration in <0.5s, mandating a dedicated UPS; the 15-second generator is too slow. Additionally, large space exterior walls facing outdoor areas must strictly reserve cable sleeves for emergency connections. | MEP_UPS_M1, Boundary_W7 | Clause 9.4.4 of T/CECS 1206-2022, Clause 9.6.3 of T/CECS 1206-2022
196 | Level-2 | To save infrastructure costs, can the facility operate the main hall using a single municipal power line with no emergency generator, allowing a 45-minute blackout window for key areas? | No. A single power line is insufficient; facilities must have dual power or emergency power backup. In the event of a sudden blackout, restoring power to key areas must strictly be completed within 30 minutes, not 45 minutes. | IfcSpace_M1, MEP_ElecRoom | Clause 9.3.1 of T/CECS 1206-2022, Clause 12.0.9 of T/CECS 1206-2022
197 | Level-2 | Can the grid power bypass the total distribution room to feed the corridor directly, and can the diesel generator be configured to run continuously even after municipal power is restored? | No. Grid and generator power should feed into a central total distribution room before being routed to specific zones. Furthermore, when municipal power recovers, the diesel generator must automatically execute a delayed shutdown, not run continuously. | MEP_Power_C1, MEP_Generator_Outdoor | Clause 9.5.1 of T/CECS 1206-2022, Clause 9.4.2 of T/CECS 1206-2022
198 | Level-2 | Is it permissible to assign all electrical loads in the main hall the exact same flat priority grade, and aggressively overload the inadequate peacetime system instead of adding a box substation? | No. Electrical loads must be specifically graded based on reliability and safety impact; a flat priority is non-compliant. If peacetime power is inadequate, the facility must supplement it (e.g., via box substations), not overload existing systems. | IfcSpace_M1, MEP_Power_M1 | Clause 9.2.1 of T/CECS 1206-2022, Clause 9.3.2 of T/CECS 1206-2022
199 | Level-2 | For the main hall retrofit, can the team pull only one low-voltage line for the ward, and provide a small UPS for the rescue equipment that depletes in 10 minutes? | No. Retrofit projects pulling from existing substations must pull two lines (one being emergency), not one. Additionally, the UPS unit provided for critical rescue equipment must be sized to supply power for no less than 30 minutes, not 10. | MEP_Power_M1, MEP_UPS_M1 | Clause 8.0.1 of T/CECS 661-2020, Clause 9.4.4 of T/CECS 1206-2022
200 | Level-2 | Can the medical vacuum pumps in the corridor and the medical HVAC in the main hall be excluded from the 15-second emergency diesel generator's calculated capacity coverage? | No. Both medical HVAC systems and critical equipment like medical vacuum pumps are explicitly mandated to be included in the calculated capacity of the emergency diesel generator, which must automatically supply them within 15 seconds. | MEP_Gas_C1, MEP_HVAC_M1 | Clause 8.0.2 of T/CECS 661-2020, Clause 9.4.2 of T/CECS 1206-2022
201 | Level-3 | For proposing the main hall as a ward zone, do its spatial capacity, the adjacent restroom sink, and the corridor HVAC unit comply with the necessary retrofitting regulations? | Yes. The main hall can be partitioned to ≤50 beds, the existing sink drain has a U-shaped water seal, and the HVAC unit complies with standards. | IfcSpace_M1, IfcSanitaryTerminal_R1_Sink, IfcAirTerminal_C1_HVAC | Clause 4.1.3.4 of WS 694-2020, Clause 5.1.2.6 of WS 696-2020, Clause 5.1.9 of WS/T 698-2020
202 | Level-3 | During the retrofitting evaluation, does the patient admission route “entering via the main door (C1_Entrance), diverging through the corridor (C1), and finally settling in the main hall (M1)” comply with screening, ventilation, and terminal capacity regulations? | Yes. The entrance door node performs strict temperature screening, the corridor HVAC unit meets hygiene management standards, and the planned bed capacity in the terminal main hall (M1) is kept under 50 bed, forming a compliant safety loop. | IfcDoor_C1_Entrance, IfcAirTerminal_C1_HVAC, IfcSpace_M1 | Clause 5.1.2 of WS/T 698-2020, Clause 5.1.9 of WS/T 698-2020, Clause 4.1.3.4 of WS 694-2020
203 | Level-3 | During the retrofitting evaluation, do the corridor's entrance door, the main hall's AHU, and the restroom's exhaust fan satisfy the baseline public health standards for safe operation? | Yes. The entrance supports temperature checks, the AHU has proper condensate U-seal drainage, and the exhaust fan provides the required strengthened ventilation. | IfcDoor_C1_Entrance, IfcAirTerminal_M1_AHU, IfcAirTerminal_R1_Exhaust | Clause 5.1.2 of WS/T 698-2020, Clause 5.1.2.6 of WS 696-2020, Clause 5.2.3 of WS/T 698-2020
204 | Level-3 | Must the independent mechanical ventilation systems for the main hall and the corridor each have a dedicated power supply, and must the main hall's pressure be strictly lower while backed by a 15-second emergency generator? | Yes. The systems must be independent with decreasing pressure toward the contaminated hall. Furthermore, their power supplies must be separately configured, and the medical zone explicitly requires a 15-second backup diesel generator. | IfcSpace_M1, IfcSpace_C1, MEP_HVAC_M1_1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.0.3 of T/CECS 661-2020, Clause 8.0.2 of T/CECS 661-2020
205 | Level-3 | When configuring the changing room L1 and the contaminated hall M1, must they have independent mechanical ventilation, with M1's exhaust vents placed below 0.3m and L1's primary changing exit delivering at least 40 ACH exhaust? | Yes. Independent mechanical ventilation is required by zone. The respiratory ward (M1) exhaust vents must be <0.3m from the floor, and the exit primary changing room (L1) explicitly mandates at least 40 air changes per hour (ACH) of exhaust. | IfcSpace_M1, IfcSpace_L1, MEP_HVAC_M1_4 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022, Clause 4.1.5.1 of WS 694-2020
206 | Level-3 | In addition to installing an air quality monitoring system in the main hall's bed area, must the centralized control ventilation units in both the hall and the corridor undergo weekly cleaning of their filters and condensate pans? | Yes. Air quality monitors are recommended for bed areas, ventilation requires centralized interlocking controls, and all operating HVAC components (including filters and pans) across all zones must undergo mandatory weekly cleaning/disinfection. | IfcSpace_M1, MEP_HVAC_M1_4, MEP_HVAC_C1_1 | Clause 9.5.8 of T/CECS 1206-2022, Clause 5.2.2.4 of WS 696-2020, Clause 5.1.2.5 of WS 696-2020
207 | Level-3 | If an outdoor lab cabin is deployed, must its independent ventilation system be documented in the facility's HVAC profile and be wired to the 15-second automatic backup diesel generator? | Yes. Lab cabins require absolutely independent ventilation. As a medical ventilation system, it must be powered by the 15s backup generator, and its fundamental design parameters must be formally collected and documented. | IfcSpace_Outdoor, IfcSpace_M1, MEP_HVAC_M1_6 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.0.2 of T/CECS 661-2020, Clause 6.1.1 of WS 696-2020
208 | Level-3 | Between the clean L1, buffer S4, and contaminated M1, must mechanical ventilation be universally installed, ensuring static pressure decreases from L1 to M1 while S4's airflow is directed solely toward M1? | Yes. Mechanical ventilation is mandatory. Static pressure must decrease sequentially toward the contaminated zone (L1 > S4 > M1), and buffer airflow must be rationally organized to flow strictly toward the contaminated zone or primary changing. | IfcSpace_S4, IfcSpace_M1, IfcSpace_L1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022, Clause 8.2.1 of T/CECS 1206-2022
209 | Level-3 | Does the exhaust fan in the main hall require a dedicated standby backup unit, a HEPA filter that is cleaned or replaced weekly, and connection to the 15-second emergency power supply? | Yes. Contaminated zone exhaust systems require standby fan units and HEPA filters. These filters require weekly maintenance, and the entire medical exhaust setup must be supported by the 15-second emergency diesel generator. | IfcSpace_M1, MEP_HVAC_M1_5, MEP_HVAC_M1_6 | Clause 8.0.2 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022, Clause 5.1.2.5 of WS 696-2020
210 | Level-3 | Can administrative office L2 use natural ventilation (opening doors/windows for 30 min every 2-3h) while the ward M1 uses independent mechanical ventilation, provided both HVAC power supplies are independently configured? | Yes. Dense offices (L2) can increase natural ventilation frequency, while the contaminated ward (M1) must strictly use independent mechanical ventilation. Regardless of the type, HVAC power supplies must be set up independently. | IfcSpace_L2, IfcSpace_M1, Connection_ExtWin_W25 | Clause 8.0.3 of T/CECS 661-2020, Clause 7.0.1 of T/CECS 661-2020, Clause 5.2.2.2 of WS 696-2020
211 | Level-3 | Must the main hall's ventilation feature a standby exhaust fan, interlocking fault alarms at the central control box, and condensate pans that undergo weekly cleaning and disinfection? | Yes. Contaminated exhaust requires standby units and interlocking motorized valves. The control box must feature fault alarms/centralized control, and the condensate pans of the AHUs require mandatory weekly disinfection. | IfcSpace_M1, MEP_HVAC_M1_2, MEP_HVAC_M1_5 | Clause 9.5.8 of T/CECS 1206-2022, Clause 8.2.4 of T/CECS 1206-2022, Clause 5.2.2.4 of WS 696-2020
212 | Level-3 | If a container lab operates inside M1, must its ventilation be independent from M1, M1's ventilation independent from C1, and all of these systems feature their own independent power supply circuits? | Yes. The lab cabin must have ventilation independent of the host space (M1). The host space (M1, contaminated) must be independent of the corridor (C1, semi-contaminated). All ventilation systems must have independent power supplies. | IfcSpace_M1, IfcSpace_C1, MEP_HVAC_M1_7 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.0.3 of T/CECS 661-2020, Clause 7.0.1 of T/CECS 661-2020
213 | Level-3 | Must Restroom R1 and Ward M1 possess independent mechanical ventilation systems whose filters are cleaned weekly, and must both rely on the 15-second emergency generator during outages? | Yes. Mechanical ventilation must be independent by zone. Filters require weekly cleaning across all operating systems, and as medical function zones, their ventilation loads must be backed by the 15-second diesel generator. | IfcSpace_R1, IfcSpace_M1, MEP_HVAC_R1 | Clause 8.0.2 of T/CECS 661-2020, Clause 4.1.5.1 of WS 694-2020, Clause 5.1.2.5 of WS 696-2020
214 | Level-3 | When collecting basic HVAC profile data for M1 and C1, must the documentation reflect their respective pressure gradients and confirm that their AHUs undergo weekly cleaning and disinfection? | Yes. HVAC profile data (types, parameters, disinfection methods) must be collected. This data will inherently reflect the mandated pressure gradient (M1 < C1) and the strict operational requirement for weekly AHU disinfection. | IfcSpace_M1, IfcSpace_C1, MEP_HVAC_M1_1 | Clause 7.0.1 of T/CECS 661-2020, Clause 6.1.1 of WS 696-2020, Clause 5.2.2.4 of WS 696-2020
215 | Level-3 | Must the fresh air system in M1 be equipped with interlocking motorized valves, run on an independent power supply, and supply no more than 80% of the exhaust air volume? | Yes. The fresh air and exhaust systems require interlocking motorized valves at inlets/outlets and independent power configurations. For respiratory wards, fresh air volume must strictly not exceed 80% of the exhaust volume. | IfcSpace_M1, MEP_HVAC_M1_1, MEP_HVAC_M1_3 | Clause 8.0.3 of T/CECS 661-2020, Clause 9.5.8 of T/CECS 1206-2022, Clause 8.2.4 of T/CECS 1206-2022
216 | Level-3 | Within an indoor lab cabin, must the PCR zone and the Prep zone have completely independent ventilation systems, 15-second backup power, and HEPA filters that are cleaned weekly? | Yes. Different protection zones within a lab cabin must have mutually independent ventilation. As medical equipment, they need 15s backup power, and all operational filters must undergo weekly cleaning or replacement. | IfcSpace_M1, MEP_HVAC_M1_7, MEP_HVAC_S3 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.0.2 of T/CECS 661-2020, Clause 5.1.2.5 of WS 696-2020
217 | Level-3 | If L1 is the primary changing room, must it have mechanical ventilation with 30 ACH supply and 40 ACH exhaust, and must its air handling units be disinfected weekly? | Yes. Infectious disease zones mandate mechanical ventilation. The exit "primary changing" specifically requires ≥30 ACH supply and ≥40 ACH exhaust, and its operating AHUs must be subjected to weekly disinfection. | IfcSpace_L1, IfcSpace_C1, MEP_HVAC_L1 | Clause 8.2.4 of T/CECS 1206-2022, Clause 8.2.1 of T/CECS 1206-2022, Clause 5.2.2.4 of WS 696-2020
218 | Level-3 | Must the exhaust vents in M1 be positioned below 0.3m, maintain a lower static pressure than C1, and be powered by the 15-second backup generator to prevent airflow reversal during outages? | Yes. M1's exhaust vents must be at the lower part (<0.3m). The pressure must be sequentially lower than C1. To guarantee this gradient never fails, the medical ventilation system must be backed by a 15-second emergency generator. | IfcSpace_M1, IfcSpace_C1, MEP_HVAC_M1_4 | Clause 8.0.2 of T/CECS 661-2020, Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022
219 | Level-3 | Must the decommissioning plan budget for restoring the main hall's floors and doors, and during execution, must the ward beds be removed prior to dismantling the HVAC terminals? | Yes. The overall plan must include the restoration scheme for existing buildings (including floors, doors, and walls). The dismantling sequence strictly mandates removing furniture and appliances (beds) before removing MEP facilities (HVAC). | IfcSpace_M1, Connection_Door_W6, MEP_HVAC_M1_1 | Clause 3.0.2 of T/CECS 1226-2022, Clause 6.1.4 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022
220 | Level-3 | Before dismantling the corridor's HVAC, must terminal disinfection pass evaluation, and if fluorescent tubes are removed from the lighting fixtures, must their final outdoor disposal site be recorded in the ledger? | Yes. Terminal disinfection must be evaluated as qualified before dismantling. Fluorescent tubes are classified as hazardous waste, and the entire transport process, explicitly including the final disposal site, must be tracked in the ledger. | MEP_HVAC_C1_1, MEP_Light_C1_1, IfcSpace_Outdoor | Clause 5.1.3 of T/CECS 1226-2022, Clause 4.1.6 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
221 | Level-3 | When dismantling the restroom plumbing after removing the patient chairs, are the PVC pipes classified as recyclable, and must the resulting wastewater be pre-treated before being discharged outdoors? | Yes. MEP (plumbing) must be dismantled after furniture (chairs). PVC pipes are explicitly classified as recyclable. Any wastewater generated from dismantling must be pre-treated by the facility's existing systems before municipal discharge. | Equipment_Toilet_3, Equipment_Chair_2, IfcSpace_Outdoor | Clause 6.1.4 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022
222 | Level-3 | Must the terminal disinfection of the main hall be qualified before transporting the epidemic waste (used masks) and other dismantled items (abandoned bedding) from the bed areas to the outdoor collection zone? | Yes. Terminal disinfection of air and surfaces must pass evaluation before any items are cleared. Used masks are classified as epidemic waste, and abandoned bedding as other dismantled items; both require disinfection prior to outdoor transport. | IfcSpace_M1, Equipment_Bed_M1, IfcSpace_Outdoor | Clause 5.1.2 of T/CECS 1226-2022, Clause 4.1.4 of T/CECS 1226-2022, Clause 4.1.5 of T/CECS 1226-2022
223 | Level-3 | Following successful terminal disinfection, if hazardous waste like filter cartridges are removed from the main hall's HVAC, must the entire corridor and hall HVAC systems be formally commissioned during restoration? | Yes. Dismantling begins only after disinfection passes. HVAC filter cartridges are strictly classified as hazardous waste. Finally, during the restoration phase, all MEP systems (including HVAC) must be recommissioned to a qualified status. | IfcSpace_M1, MEP_HVAC_M1_4, IfcSpace_C1 | Clause 5.1.3 of T/CECS 1226-2022, Clause 4.1.6 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
224 | Level-3 | Should the overall project scheme estimate the volume of recyclable PVC bed partitions to be dismantled, while also including a comprehensive plan to restore the corridor's original floors and exterior glass windows? | Yes. The overall decommissioning plan must estimate waste volumes and include building restoration schemes. PVC partitions are defined as recyclable materials, and restoring existing buildings explicitly mandates recovering floors and glass windows. | Boundary_W55, Boundary_Floor_C1, Connection_ExtWin_W25 | Clause 3.0.2 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022
225 | Level-3 | Must the locker room chairs be removed prior to dismantling its electrical fixtures, and must the electrical system be later recommissioned while tracking all waste transport vehicles in the official ledger? | Yes. Furniture must be removed before MEP electrical systems. The ledger must record all waste transport vehicle information, and the restoration rules strictly mandate that electrical systems must be recommissioned to a qualified state. | Equipment_TableChairSet_L2, MEP_Light_L2, IfcSpace_Outdoor | Clause 6.1.4 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
226 | Level-3 | Must terminal disinfection pass before clearing medical waste from the main hall and before dismantling the restroom toilets, and must wastewater from toilet removal be pre-treated before municipal discharge? | Yes. Clearing items requires qualified terminal disinfection, and physical dismantling also requires qualified terminal disinfection. Wastewater from toilet dismantling must be pre-treated before outdoor discharge. | IfcSpace_M1, Equipment_Toilet_3, IfcSpace_Outdoor | Clause 5.1.2 of T/CECS 1226-2022, Clause 5.1.3 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022
227 | Level-3 | When sorting waste, are the used gloves near the beds classified as epidemic waste, the corridor's cable trays as recyclable, and the outdoor paint buckets as hazardous waste? | Yes. Used gloves are explicitly defined as epidemic-related waste. Cable trays from MEP installations are classified as recyclable dismantled materials. Waste paint buckets and their packaging are strictly categorized as hazardous waste. | Equipment_Bed_M1, MEP_HVAC_C1_1, IfcSpace_Outdoor | Clause 4.1.4 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022, Clause 4.1.6 of T/CECS 1226-2022
228 | Level-3 | Must the overall decommissioning scheme cover the restoration of the main hall's exterior walls and doors, and must the entire transport and disposal process for these materials be logged in the ledger? | Yes. The overall scheme must plan for restoring the existing site (walls, doors). Concurrently, a full-process ledger must be established to record the transport volumes, vehicles, and final disposal locations of all dismantled materials. | Boundary_W7, Connection_Door_W7, IfcSpace_Outdoor | Clause 3.0.2 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
229 | Level-3 | Must the original floor drains in the main hall be sealed before operation, must its HVAC condensate be drained indirectly, and must the condensate pipe U-traps be checked weekly? | Yes. Construction rules mandate sealing existing floor drains. HVAC condensate from contaminated areas must be discharged indirectly into sewage. Operation protocols require weekly checks of the U-trap water seals to prevent dry-out. | Boundary_Floor_M1, MEP_HVAC_M1_2, MEP_Drainage_M1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 4.3.4 of T/CADBM 72-2023, Clause 5.1.2.6 of WS 696-2020
230 | Level-3 | Are the outdoor supply and drainage pipes required to maintain a 1m horizontal gap, while the main hall's vent pipe must be >4m from fresh air intakes and equipped with a HEPA filter? | Yes. Outdoor water supply and drainage pipes must have a horizontal clearance of ≥1m. Additionally, contaminated zone vent exits must maintain a >4.0m distance from fresh air intakes and be fitted with HEPA filters. | MEP_Supply_Outdoor, MEP_VentPipe_M1, MEP_FreshAir_M1_1 | Clause 5.2.9 of T/CADBM 72-2023, Clause 7.4.3 of T/CECS 1206-2022, Clause 6.0.7 of T/CECS 661-2020
231 | Level-3 | Should the drainage pipes in Corridor C1 and Restroom R1 undergo closed-water tests, be surface-mounted indoors, and be strictly sealed if retained after facility decommissioning? | Yes. Drainage pipes mandate closed-water tests. Indoor plumbing in emergency facilities should be surface-mounted. If temporary drainage pipes are not dismantled after decommissioning, they must be securely sealed. | MEP_Drainage_C1, MEP_Drainage_R1, IfcSpace_C1 | Clause 4.3.6 of T/CADBM 72-2023, Clause 11.3.2 of T/CECS 1206-2022, Clause 13.2.2 of T/CECS 1206-2022
232 | Level-3 | In a containerized restroom, must the toilets be installed adjacent to exterior walls, must horizontal public sewage pipes have cleanouts, and must shower wastewater bypass the absent septic tank via sealed pipes? | Yes. Container cabins require sanitary fixtures against exterior walls. Public restroom horizontal pipe ends require cleanouts. If a septic tank is unfeasible, shower wastewater must be collected via sealed pipes and disinfected separately. | Equipment_Toilet_3, Boundary_W12, Equipment_Shower_R1 | Clause 3.2.12 of T/CADBM 72-2023, Clause 5.3.6 of T/CADBM 72-2023, Clause 4.3.1 of T/CADBM 72-2023
233 | Level-3 | Since the main hall doesn't require flushing, is installing floor drains prohibited, and must Corridor C1's vent pipe use the same material as its drain and exhaust at high altitude? | Yes. Floor drains are strictly prohibited in non-flushing dry areas. The vent pipe material should match the plastic/cast iron drainage pipe, and sewage vent tailgas must be discharged at a high altitude away from people. | Boundary_Floor_M1, MEP_Drainage_C1, MEP_VentPipe_C1 | Clause 4.3.9 of T/CADBM 72-2023, Clause 3.3.3 of T/CADBM 72-2023, Clause 4.3.13 of T/CADBM 72-2023
234 | Level-3 | Does the main hall's drainage system require strict anti-leakage measures and closed-water tests, while its vent exhaust must be placed >4.0m from fresh air intakes and equipped with sterilization devices? | Yes. Drainage systems require closed-water tests and anti-leakage measures. Furthermore, isolation zone vent pipe exits must be equipped with sterilization or HEPA filtration devices and kept at least 4.0m away from fresh air intakes. | MEP_Drainage_M1, MEP_VentPipe_M1, MEP_FreshAir_M1_1 | Clause 6.0.8 of T/CECS 661-2020, Clause 7.4.3 of T/CECS 1206-2022, Clause 6.0.7 of T/CECS 661-2020
235 | Level-3 | Must the containerized Restroom R1 undergo a water spray test, maintain a 0.5m horizontal indoor gap between supply and drain pipes, and install cleanouts on horizontal pipes connecting 3+ sinks? | Yes. Container cabins must undergo water spray leak testing. Indoor parallel water supply and drain pipes require ≥0.5m horizontal clearance. Horizontal sewage pipes connecting 3 or more fixtures (sinks) mandate cleanouts. | IfcSpace_R1, MEP_Supply_R1, Equipment_Sink_3 | Clause 3.2.12 of T/CADBM 72-2023, Clause 5.2.9 of T/CADBM 72-2023, Clause 5.3.6 of T/CADBM 72-2023
236 | Level-3 | Are the Corridor C1 drainage pipes required to pass a closed-water test using hot-melt connections, while the main hall's original drains are sealed and its HVAC U-traps checked weekly? | Yes. Drain pipes need closed-water testing and hot-melt leak-proof connections. Construction prep requires sealing original floor drains in M1, and operations require weekly water replenishment checks for HVAC U-traps. | MEP_Drainage_C1, Boundary_Floor_M1, MEP_HVAC_M1_2 | Clause 4.3.6 of T/CADBM 72-2023, Clause 11.3.2 of T/CECS 1206-2022, Clause 5.1.2.6 of WS 696-2020
237 | Level-3 | In the outdoor layout, must rainwater and sewage be strictly separated, while the indoor vent pipe matches the drainage pipe's material and exhausts its tailgas at high altitude? | Yes. Outdoor rainwater and sewage networks must adopt a separate flow system. The vent pipes are advised to use the same material as drainage pipes, and their tailgas must be exhausted at a high altitude safely away from activities. | IfcSpace_Outdoor, MEP_VentPipe_M1, MEP_Drainage_M1 | Clause 4.3.1 of T/CADBM 72-2023, Clause 3.3.3 of T/CADBM 72-2023, Clause 4.3.13 of T/CADBM 72-2023
238 | Level-3 | If the temporary drainage pipes are decommissioned, must they be completely sealed, just as floor drains were forbidden in the non-flushing main hall, and must the hall's HVAC condensate be drained indirectly? | Yes. Decommissioned retained pipes must be sealed. Floor drains are explicitly forbidden in dry areas like the main hall without flushing needs. Additionally, condensate from contaminated zones must drain indirectly into the sewage. | MEP_Drainage_M1, Boundary_Floor_M1, MEP_HVAC_M1_2 | Clause 13.2.2 of T/CECS 1206-2022, Clause 4.3.9 of T/CADBM 72-2023, Clause 4.3.4 of T/CADBM 72-2023
239 | Level-3 | In a partitioned zone capped at 50 beds, must each bed maintain a >1.2m spacing, be equipped with 3 combo power sockets, and feature 2 medical oxygen terminals? | Yes. Zoning strictly caps beds at 50 per area with >1.2m spacing. Furthermore, each bed must have three 220V/10A combo sockets at the headboard, and exactly 2 medical oxygen terminals must be provided per bed. | IfcSpace_M1, MEP_Power_M1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 9.5.6 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020
240 | Level-3 | If peacetime lighting causes glare in the gender-separated ward, must new overhead lights be installed away from directly above the beds, and must individual bedside lamps be provided? | Yes. Wards must be gender-separated. If peacetime lighting causes glare, separate anti-glare overhead lights must be installed, avoiding the space directly above beds. Additionally, each bed mandates a bedside or desk lamp. | Equipment_Bed_M1, MEP_Light_M1_1, MEP_Light_M1_2 | Clause 4.1.3.4 of WS 694-2020, Clause 9.7.3 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
241 | Level-3 | To preserve the building's peacetime utility, must the temporary water dispensers be reasonably distributed per nursing unit, and the oxygen design flow calculated for 100% simultaneous use? | Yes. The conversion must not permanently impair peacetime functions. Operationally, drinking water points must be reasonably established per nursing unit, and medical oxygen must be rigorously designed for a 100% simultaneous usage rate. | IfcSpace_M1, Equipment_WaterDispenser_M1, MEP_Gas_M1 | Clause 3.0.1 of T/CECS 1206-2022, Clause 7.3.6 of T/CECS 1206-2022, Clause 9.0.4 of T/CECS 661-2020
242 | Level-3 | Must every patient bed be provided with a bedside table, feature a desk lamp plugged into one of its three 220V bedside sockets, and be spaced >1.2m from adjacent beds? | Yes. Beds must be >1.2m apart and equipped with personal items like bedside tables. The bedhead requires three 220V combo sockets, which can be utilized to power the explicitly mandated bedside desk lamp. | Equipment_Bed_M1, MEP_Power_M1, MEP_Light_M1_2 | Clause 4.1.3.4 of WS 694-2020, Clause 9.5.6 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
243 | Level-3 | Does each bed unit require anti-glare overhead lighting, at least 1 medical vacuum terminal, and 3 combo power sockets including one with a USB port? | Yes. Overhead lighting must incorporate anti-glare measures. Medically, beds require ≥1 vacuum terminal (and 2 oxygen). Electrically, the three 220V sockets at the bedhead should include at least one USB charging port. | MEP_Light_M1_1, MEP_Gas_M1, MEP_Power_M1 | Clause 9.7.3 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020, Clause 9.5.6 of T/CECS 1206-2022
244 | Level-3 | In a 50-bed nursing unit where patients are >1.2m apart, must there be dedicated drinking water points and an oxygen system sized for 100% simultaneous usage? | Yes. The zone adheres to the maximum 50-bed and >1.2m spacing rules. Concurrently, it must possess dedicated drinking water points (electric boilers/bottled water) and an oxygen supply system calculated for 100% simultaneous patient use. | IfcSpace_M1, Equipment_WaterDispenser_M1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 7.3.6 of T/CECS 1206-2022, Clause 9.0.4 of T/CECS 661-2020
245 | Level-3 | While ensuring the building's peacetime use is unaffected, must public areas feature cleaning sockets and each bed feature exactly 2 medical oxygen terminals? | Yes. The conversion must undergo assessment to protect peacetime functions. In the operational layout, public areas require sockets for cleaning/smart devices, and each individual bed strictly requires 2 medical oxygen terminals. | IfcSpace_M1, MEP_Power_C1, MEP_Gas_M1 | Clause 3.0.1 of T/CECS 1206-2022, Clause 9.5.6 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020
246 | Level-3 | Must the beds be provided with personal trash cans and storage, avoid direct overhead glare lighting, and have their oxygen flow designed for 100% simultaneous use? | Yes. Each bed unit must include personal necessities (trash cans, storage boxes). Overhead lighting must not be placed directly above the bed to avoid glare. Finally, the medical oxygen system design must assume 100% simultaneous utilization. | Equipment_Bed_M1, MEP_Light_M1_1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 9.7.3 of T/CECS 1206-2022, Clause 9.0.4 of T/CECS 661-2020
247 | Level-3 | If peacetime power is insufficient, must the outdoor supplementary generator route its cables through reserved exterior wall sleeves and feed directly into the total distribution room? | Yes. Inadequate peacetime power can be supplemented by a generator. Cables from outdoor emergency facilities must pass through reserved sleeves in exterior walls facing the plaza, and then feed directly into the central total distribution room. | MEP_Generator_Outdoor, Boundary_W7, MEP_ElecRoom | Clause 9.3.2 of T/CECS 1206-2022, Clause 9.6.3 of T/CECS 1206-2022, Clause 9.5.1 of T/CECS 1206-2022
248 | Level-3 | For a retrofit pulling two lines from the substation, must the rescue room's critical devices have a >30min UPS, and must the diesel generator cover its load within 15 seconds? | Yes. Retrofits can pull two lines (one being emergency). Critical rescue equipment requires a UPS lasting ≥30 minutes. Concurrently, the overall rescue room load must be backed by a diesel generator that auto-starts within 15 seconds. | MEP_Power_Main, MEP_UPS_M1, MEP_Generator_Outdoor | Clause 8.0.1 of T/CECS 661-2020, Clause 9.4.4 of T/CECS 1206-2022, Clause 8.0.2 of T/CECS 661-2020
249 | Level-3 | Lacking dual grid power, must the facility install an outdoor generator that auto-starts in 15s to guarantee 24-hour uninterrupted power and restore key areas within 30 minutes? | Yes. Without dual grid power, emergency power is mandatory. The generator must auto-start in 15 seconds. This setup is crucial to satisfy the overarching mandate of 24h uninterrupted power and <30-minute restoration for key areas. | MEP_Power_Main, MEP_Generator_Outdoor, IfcSpace_M1 | Clause 9.3.1 of T/CECS 1206-2022, Clause 9.4.2 of T/CECS 1206-2022, Clause 12.0.9 of T/CECS 1206-2022
250 | Level-3 | Must the electrical loads for M1's HVAC and lighting be prioritized by reliability grades, set on circuits independent from peacetime use, and covered by the 15-second generator? | Yes. Electrical loads must be graded by reliability. Epidemic power circuits must be independent from peacetime circuits. Both medical HVAC and ward lighting/power must be explicitly covered by the 15-second emergency diesel generator. | MEP_Power_M1, MEP_HVAC_M1, MEP_Generator_Outdoor | Clause 9.2.1 of T/CECS 1206-2022, Clause 9.3.3 of T/CECS 1206-2022, Clause 8.0.2 of T/CECS 661-2020
251 | Level-3 | To increase fresh air, is it compliant to shut off M1's HVAC and open its exterior windows for 30 minutes every 2 hours, utilizing the shared power circuit from the lighting system? | No. M1 is a contaminated ward where opening windows destroys negative pressure. Furthermore, sharing power with lighting violates the requirement for independent HVAC power supplies, removing the 15s backup guarantee. | IfcSpace_M1, Connection_ExtWin_W25, MEP_Light_M1_1 | Clause 8.0.3 of T/CECS 661-2020, Clause 8.0.2 of T/CECS 661-2020, Clause 5.2.2.2 of WS 696-2020
252 | Level-3 | Can buffer room S2 share its mechanical exhaust duct with ward M1 to ensure M1's fresh air exceeds its exhaust volume, thus creating a strong positive pressure pushing toward the corridor C1? | No. Zones must have independent systems. Ward M1's fresh air must NOT exceed 80% of exhaust, and static pressure must decrease toward M1; creating positive pressure pushing toward C1 directly violates airflow safety. | IfcSpace_S2, IfcSpace_M1, IfcSpace_C1 | Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022, Clause 4.1.5.1 of WS 694-2020
253 | Level-3 | To save equipment costs, can the container lab in M1 merge its exhaust with M1's main exhaust to utilize M1's standby fan and centralized interlocking control system? | No. The lab cabin's ventilation must be strictly independent from the host space to prevent cross-contamination. Merging ducts violates this fundamental independence rule, even if M1 possesses standby fans and central controls. | IfcSpace_M1, MEP_HVAC_M1_5, MEP_HVAC_M1_7 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 9.5.8 of T/CECS 1206-2022, Clause 8.2.4 of T/CECS 1206-2022
254 | Level-3 | Is it permissible to skip mechanical ventilation in the changing room L1 and rely solely on the negative pressure draw from M1, avoiding the need for a 15-second backup generator for L1? | No. Mechanical ventilation is explicitly mandatory for all infectious disease areas (including changing rooms). Relying on adjacent negative pressure is prohibited, and L1's required medical ventilation must have 15s backup. | IfcSpace_L1, IfcSpace_M1, MEP_HVAC_L1 | Clause 8.0.2 of T/CECS 661-2020, Clause 7.0.1 of T/CECS 661-2020, Clause 8.2.1 of T/CECS 1206-2022
255 | Level-3 | Is the facility compliant if C1's exhaust filters are cleaned monthly while M1's exhaust vents are mounted near the ceiling at 2.5m high to maximize fresh air mixing? | No. Filters must be cleaned weekly, not monthly. Furthermore, in the respiratory contaminated ward (M1), exhaust vents must be uniformly placed at the bottom, not higher than 0.3m from the floor, to capture sinking droplets. | IfcSpace_C1, IfcSpace_M1, MEP_HVAC_M1_4 | Clause 8.2.4 of T/CECS 1206-2022, Clause 5.2.2.4 of WS 696-2020, Clause 5.1.2.5 of WS 696-2020
256 | Level-3 | To simplify the collected HVAC profile data, can M1 and C1 share a single power supply circuit, and can M1's fresh air volume be tuned to 100% of its exhaust volume? | No. HVAC power supplies must be independent. M1's fresh air volume must strictly be ≤80% of its exhaust to maintain negative pressure. Simplifying documentation does not justify violating structural safety codes. | IfcSpace_M1, IfcSpace_C1, MEP_HVAC_M1_1 | Clause 8.0.3 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022, Clause 6.1.1 of WS 696-2020
257 | Level-3 | Can the centralized interlocking control system automatically shut down M1's mechanical exhaust every 3 hours to allow patients to open exterior windows for 30 minutes of natural ventilation? | No. Opening windows for natural ventilation in a contaminated respiratory ward destroys the mandatory negative pressure gradient. The mechanical ventilation and centralized interlocking systems must run continuously. | IfcSpace_M1, Connection_ExtWin_W25, MEP_HVAC_M1_2 | Clause 7.0.1 of T/CECS 661-2020, Clause 9.5.8 of T/CECS 1206-2022, Clause 5.2.2.2 of WS 696-2020
258 | Level-3 | If a lab cabin is installed inside M1, can it establish its negative pressure by linking its exhaust ducts directly to M1's exhaust, thereby sharing M1's 15-second emergency generator? | No. While it needs the 15s emergency generator, the lab cabin must have an entirely independent ventilation system. Linking exhaust ducts with M1 violates the strict independence requirement to prevent aerosol diffusion. | IfcSpace_M1, MEP_HVAC_M1_7, MEP_HVAC_M1_3 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.0.2 of T/CECS 661-2020, Clause 7.0.1 of T/CECS 661-2020
259 | Level-3 | Can buffer S4 be designed such that its airflow is directed outward toward the clean corridor C1, while its independent exhaust system operates without any mechanical supply fans? | No. Buffer airflow must be rationally directed toward the contaminated zone or primary changing, never back toward the clean corridor. Proper mechanical ventilation systems require balanced supply and exhaust, not just exhaust. | IfcSpace_S4, IfcSpace_C1, MEP_HVAC_S4 | Clause 8.2.4 of T/CECS 1206-2022, Clause 8.2.1 of T/CECS 1206-2022, Clause 4.1.5.1 of WS 694-2020
260 | Level-3 | Is it acceptable for the independent HVAC in M1 and S3 to share a power distribution box, provided the facility completely seals the AHUs and never cleans their filters to avoid exposure? | No. HVAC power supplies must be configured independently (no shared boxes). Moreover, permanently sealing AHUs is prohibited; regulations mandate weekly cleaning, disinfection, or replacement of AHU components and filters. | IfcSpace_M1, IfcSpace_S3, MEP_HVAC_M1_6 | Clause 8.0.3 of T/CECS 661-2020, Clause 5.2.2.4 of WS 696-2020, Clause 5.1.2.5 of WS 696-2020
261 | Level-3 | Can the exhaust system in M1 be installed without a standby fan unit, without centralized interlocking controls, and without being wired to the 15-second diesel generator to reduce initial construction costs? | No. This violates three critical redundancies: contaminated exhaust systems mandate standby fans, must have interlocking controls/fault alarms, and strictly require connection to the 15-second automatic backup diesel generator. | IfcSpace_M1, MEP_HVAC_M1_5, MEP_HVAC_M1_2 | Clause 8.0.2 of T/CECS 661-2020, Clause 9.5.8 of T/CECS 1206-2022, Clause 8.2.4 of T/CECS 1206-2022
262 | Level-3 | In the lab cabin, can the PCR zone and reagent prep zone share a single ventilation system if they install a large HEPA filter that is cleaned bi-weekly instead of weekly? | No. Different protection zones within the lab MUST have independent ventilation systems (cannot share). Furthermore, maintenance codes strictly require the filters to be cleaned or replaced weekly, not bi-weekly. | IfcSpace_M1, MEP_HVAC_M1_7, MEP_HVAC_S3 | Clause 5.4.1.4 of T/CIQA 16-2021, Clause 8.2.4 of T/CECS 1206-2022, Clause 5.1.2.5 of WS 696-2020
263 | Level-3 | Can the densely populated office L2 tap into M1's independent mechanical ventilation system to get fresh air, allowing staff to avoid opening L2's windows every 2 hours? | No. The mechanical ventilation for the contaminated ward (M1) must be strictly independent; clean offices (L2) cannot tap into it. For L2, staff are explicitly encouraged/required to open windows or use natural ventilation every 2-3 hours. | IfcSpace_L2, IfcSpace_M1, MEP_HVAC_M1_1 | Clause 7.0.1 of T/CECS 661-2020, Clause 4.1.5.1 of WS 694-2020, Clause 5.2.2.2 of WS 696-2020
264 | Level-3 | For the primary changing room L1, is it compliant to install an exhaust system delivering only 20 ACH, powered by the main lighting circuit, as long as it has mechanical supply fans? | No. The exit "primary changing" room mandates a minimum of 40 ACH of exhaust (20 is insufficient). Additionally, its power supply must be independently configured and cannot share the main lighting circuit. | IfcSpace_L1, MEP_HVAC_L1, MEP_Light_L1_1 | Clause 8.0.3 of T/CECS 661-2020, Clause 8.2.4 of T/CECS 1206-2022, Clause 8.2.1 of T/CECS 1206-2022
265 | Level-3 | To quickly purge odors, can the interlocking controls be overridden to make M1's static pressure higher than C1's, while also skipping the weekly condensate pan disinfection? | No. The static pressure must always decrease from semi-contaminated (C1) to contaminated (M1). Overriding interlocking controls to make M1 positive, and skipping the mandatory weekly disinfection of condensate pans are severe violations. | IfcSpace_M1, IfcSpace_C1, MEP_HVAC_M1_2 | Clause 7.0.1 of T/CECS 661-2020, Clause 9.5.8 of T/CECS 1206-2022, Clause 5.2.2.4 of WS 696-2020
266 | Level-3 | Can the team skip terminal disinfection in the main hall to rapidly clear out "other waste" like bedding, and immediately dismantle the HVAC terminals before removing the patient beds? | No. Skipping terminal disinfection before clearing items violates Clause 5.1.2. Dismantling HVAC before removing furniture (beds) directly violates the mandated sequence. Bedding is defined as "other waste," but it still requires prior disinfection. | IfcSpace_M1, Equipment_Bed_M1, MEP_HVAC_M1_1 | Clause 5.1.2 of T/CECS 1226-2022, Clause 6.1.4 of T/CECS 1226-2022, Clause 4.1.5 of T/CECS 1226-2022
267 | Level-3 | Is it permissible to crush hazardous waste like fluorescent tubes from the hall into the toilet and discharge it outdoors without pre-treatment, while leaving the hall's electrical system un-commissioned? | No. Fluorescent tubes are hazardous waste and cannot be improperly disposed of. Wastewater from dismantling must be pre-treated (cannot be directly discharged). Furthermore, electrical systems must be formally commissioned during restoration. | MEP_Light_M1_2, Equipment_Toilet_4, IfcSpace_Outdoor | Clause 4.1.6 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
268 | Level-3 | Does the overall plan allow used surgical gloves from the main hall to be classified as recyclable materials, grouping them with the corridor's PVC pipes to bypass estimating separate waste volumes? | No. Used medical gloves are strictly classified as epidemic-related waste, not recyclables (unlike PVC pipes). Mixing them is dangerous, and the overall plan must explicitly estimate the generated volumes for each specific category of waste. | IfcSpace_M1, Equipment_Bed_M1, MEP_HVAC_C1_1 | Clause 4.1.4 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022, Clause 3.0.2 of T/CECS 1226-2022
269 | Level-3 | Can the demolition team dismantle the corridor doors before terminal disinfection passes, bypass restoring the main hall's floors, and deliberately omit the waste vehicle information from the ledger? | No. Dismantling cannot begin until terminal disinfection passes. Restoring existing buildings mandates recovering floors. The full-process ledger explicitly requires recording the information of all waste transport vehicles. | Connection_Door_W6, Boundary_Floor_M1, IfcSpace_Outdoor | Clause 5.1.3 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
270 | Level-3 | Is it acceptable to dismantle the main hall's HVAC before removing the beds, classify the used HVAC HEPA filters as standard recyclables, and physically install new HVAC without commissioning it? | No. MEP (HVAC) must be dismantled after furniture (beds). Used filters are strictly classified as hazardous waste, not standard recyclables. Restored HVAC systems must be formally commissioned, not just physically installed. | MEP_HVAC_M1_4, Equipment_Bed_M1, IfcSpace_M1 | Clause 6.1.4 of T/CECS 1226-2022, Clause 4.1.6 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
271 | Level-3 | Can used surgical masks found in the corridor be defined as recyclables (like concrete), allowing them to be cleared out alongside the main hall's bedding before performing terminal disinfection? | No. Surgical masks are epidemic waste, not recyclables. Leftover bedding is "other waste." Most importantly, neither can be transported out of the cabin before the terminal disinfection of the air and surfaces is evaluated and passed. | IfcSpace_C1, IfcSpace_M1, Equipment_Bed_M1 | Clause 4.1.4 of T/CECS 1226-2022, Clause 4.1.3 of T/CECS 1226-2022, Clause 5.1.2 of T/CECS 1226-2022
272 | Level-3 | Can the plumbers remove the restroom toilets before the chairs are cleared, discharge the dismantling wastewater directly to the outdoor drain, and record only the disposal site (no vehicle info) in the ledger? | No. Furniture (chairs) must be removed before plumbing (toilets). Wastewater must be pre-treated using existing facilities, not directly discharged. The ledger must comprehensively record both the final disposal site and the vehicle information. | Equipment_Toilet_3, Equipment_Chair_2, IfcSpace_Outdoor | Clause 6.1.4 of T/CECS 1226-2022, Clause 9.1.3 of T/CECS 1226-2022, Clause 3.0.3 of T/CECS 1226-2022
273 | Level-3 | Can the overall scheme exclude the restoration of the main hall's exterior windows, and can the physical dismantling of the main hall's partitions begin before the site's terminal disinfection is evaluated? | No. The overall scheme must encompass the full restoration of existing buildings, which explicitly includes doors and glass windows. Furthermore, no structural dismantling (like partitions) can commence until terminal disinfection passes. | Connection_ExtWin_W25, Boundary_W55, IfcSpace_M1 | Clause 3.0.2 of T/CECS 1226-2022, Clause 6.3.2 of T/CECS 1226-2022, Clause 5.1.3 of T/CECS 1226-2022
274 | Level-3 | Are the abandoned bedding items in the main hall considered hazardous waste (like batteries), and can the restored electrical systems in the main hall be used immediately without formal commissioning? | No. Bedding is classified as "other dismantled items" (Clause 4.1.5), whereas batteries are hazardous waste (Clause 4.1.6). Restored MEP equipment, including electrical systems, must be strictly commissioned to a qualified state before use. | Equipment_Bed_M1, MEP_Light_M1_1, IfcSpace_M1 | Clause 4.1.5 of T/CECS 1226-2022, Clause 4.1.6 of T/CECS 1226-2022, Clause 6.3.3 of T/CECS 1226-2022
275 | Level-3 | To save time, can the demolition team dismantle the ward partitions first, then clear out the epidemic waste near the beds, and only perform terminal disinfection of the main hall at the very end of the project? | No. This completely inverts the safety protocol. Terminal disinfection must occur first and pass evaluation before any items are cleared. Furthermore, partitions (Step 3) can only be dismantled after furniture and MEP systems have been removed. | Boundary_W55, Equipment_Bed_M1, IfcSpace_M1 | Clause 5.1.2 of T/CECS 1226-2022, Clause 5.1.3 of T/CECS 1226-2022, Clause 6.1.4 of T/CECS 1226-2022
276 | Level-3 | Can Corridor C1's drainage pipes be concealed in the walls, skip the mandatory closed-water test to save time, and have their U-traps checked only once a month? | No. Indoor plumbing should be surface-mounted, not concealed. Closed-water tests are mandatory to prevent leaks. U-traps for drains and condensate must be checked weekly, not monthly. All three actions violate the standards. | MEP_Drainage_C1, IfcSpace_C1, MEP_Drainage_M1 | Clause 11.3.2 of T/CECS 1206-2022, Clause 6.0.8 of T/CECS 661-2020, Clause 5.1.2.6 of WS 696-2020
277 | Level-3 | Is it compliant to install toilets in the center of the containerized restroom, and exhaust their vent pipe 1m away from the main hall's fresh air intake without a HEPA filter? | No. Sanitary facilities in container cabins must adjoin exterior walls (not central). Vent pipe exits must be ≥4.0m from fresh air intakes (not 1m), and isolation zone vents must possess HEPA filters. | Equipment_Toilet_3, MEP_VentPipe_R1, MEP_FreshAir_M1_1 | Clause 3.2.12 of T/CADBM 72-2023, Clause 7.4.3 of T/CECS 1206-2022, Clause 6.0.7 of T/CECS 661-2020
278 | Level-3 | Can the main hall's HVAC condensate be directly piped to sewage, a floor drain be installed in the dry hall, and the outdoor sewage merge with the rainwater network? | No. HVAC condensate from contaminated areas must discharge indirectly. Floor drains are strictly forbidden on non-flushing dry floors. Outdoor rainwater and sewage systems must be separated and cannot be merged. | MEP_HVAC_M1_2, Equipment_FloorDrain_M1, IfcSpace_Outdoor | Clause 4.3.4 of T/CADBM 72-2023, Clause 4.3.9 of T/CADBM 72-2023, Clause 4.3.1 of T/CADBM 72-2023
279 | Level-3 | Indoors, can a water supply pipe pass directly under a drainage pipe without a casing, while horizontal pipe ends lack cleanouts and the vent pipe uses a completely different material? | No. If supply crosses under drainage, it MUST have a protective casing ≥3x pipe diameter. Horizontal pipe ends in public restrooms mandate cleanouts. Vent pipes should match the drainage pipe's material (plastic or cast iron). | MEP_Supply_R1, MEP_Drainage_R1, MEP_VentPipe_R1 | Clause 5.2.9 of T/CADBM 72-2023, Clause 5.3.6 of T/CADBM 72-2023, Clause 3.3.3 of T/CADBM 72-2023
280 | Level-3 | Can decommissioned temporary pipes be left open, the main hall's original floor drains be used for mop water, and the vent pipe exhaust at ground level near the staff entrance? | No. Decommissioned retained pipes must be sealed. Original floor drains must be sealed before use. Vent tailgas from sewage systems must be exhausted at high altitude and strictly kept away from personnel activity areas. | MEP_Drainage_M1, Equipment_FloorDrain_M1, MEP_VentPipe_M1 | Clause 13.2.2 of T/CECS 1206-2022, Clause 11.3.2 of T/CECS 1206-2022, Clause 4.3.13 of T/CADBM 72-2023
281 | Level-3 | Can the facility bypass the closed-water tests for indoor pipes, check the condensate U-traps only during monthly maintenance, and lay outdoor supply and drainage pipes with a mere 0.2m horizontal clearance? | No. Closed-water tests are mandatory (cannot be bypassed). U-traps must be checked weekly (not monthly). Outdoor water supply and drainage pipelines must maintain a minimum horizontal clearance of 1.0m (not 0.2m). | MEP_Drainage_C1, MEP_Drainage_M1, MEP_Supply_Outdoor | Clause 4.3.6 of T/CADBM 72-2023, Clause 5.1.2.6 of WS 696-2020, Clause 5.2.9 of T/CADBM 72-2023
282 | Level-3 | Can the containerized restroom bypass the water spray test, discharge shower wastewater directly into the outdoor soil since there's no septic tank, and omit cleanouts on pipes linking 4 sinks? | No. Container cabins must perform water spray tests. Shower wastewater must be collected via sealed pipes and disinfected (not dumped in soil). Horizontal sewage pipes connecting 3 or more fixtures (4 sinks) must install cleanouts. IfcSpace_R1, Equipment_Shower_R1, Equipment_Sink_3 | IfcSpace_R1, Equipment_Shower_R1, Equipment_Sink_3 | Clause 3.2.12 of T/CADBM 72-2023, Clause 4.3.1 of T/CADBM 72-2023, Clause 5.3.6 of T/CADBM 72-2023
283 | Level-3 | Is it permissible to directly connect the main hall's HVAC condensate to the sewage line, while exhausting its vent pipe exactly 2 meters from the fresh air intake without any sterilization filter? | No. Contaminated condensate must discharge indirectly, not directly. The vent exhaust must be ≥4.0m from fresh air intakes (not 2m), and isolation zone vents must possess HEPA filters or sterilization devices. | MEP_HVAC_M1_2, MEP_VentPipe_M1, MEP_FreshAir_M1_1 | Clause 4.3.4 of T/CADBM 72-2023, Clause 7.4.3 of T/CECS 1206-2022, Clause 6.0.7 of T/CECS 661-2020
284 | Level-3 | Can a floor drain be installed in the dry main hall for future contingencies, its indoor supply plumbing concealed within the walls, and its vent exhaust placed at ground level? | No. Floor drains are prohibited in non-flushing dry spaces. Emergency facility indoor plumbing should be surface-mounted, not concealed. Sewage tailgas must be exhausted at high altitude, not ground level. | Boundary_Floor_M1, MEP_Supply_M1, MEP_VentPipe_M1 | Clause 4.3.9 of T/CADBM 72-2023, Clause 11.3.2 of T/CECS 1206-2022, Clause 4.3.13 of T/CADBM 72-2023
285 | Level-3 | Can the outdoor sewage merge into the rainwater system, the indoor vent pipe use carbon steel instead of PVC, and the decommissioned temporary pipes be left completely unsealed? | No. Outdoor systems must be separated (never merged). Vent pipes should match the plastic/cast iron material of the drainage pipes. Decommissioned temporary pipes that remain on-site must be securely sealed. | IfcSpace_Outdoor, MEP_VentPipe_C1, MEP_Drainage_C1 | Clause 4.3.1 of T/CADBM 72-2023, Clause 3.3.3 of T/CADBM 72-2023, Clause 13.2.2 of T/CECS 1206-2022
286 | Level-3 | Can we space beds 1.0m apart if we compensate by providing 4 power sockets and sharing 1 oxygen terminal between two beds? | No. Bed spacing must strictly be >1.2m, not 1.0m. While providing extra sockets is fine, sharing oxygen is strictly forbidden; every single bed must independently possess exactly 2 medical oxygen terminals. | Equipment_Bed_M1, MEP_Power_M1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 9.5.6 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020
287 | Level-3 | Is it acceptable to place 60 beds in a single zone, install high-intensity overhead lights directly above them, and omit bedside lamps entirely? | No. A single zone is capped at 50 beds (not 60). Installing lighting directly overhead causing glare is strictly prohibited. Furthermore, every bed is explicitly required to have a dedicated bedside lamp or desk lamp. | IfcSpace_M1, MEP_Light_M1_1, MEP_Light_M1_2 | Clause 4.1.3.4 of WS 694-2020, Clause 9.7.3 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
288 | Level-3 | To save costs and permanently alter the structure, can we limit drinking water to one point for the whole building and calculate oxygen for only 50% simultaneous use? | No. Permanent structural alterations that destroy peacetime functions are forbidden. Water points must be reasonably distributed by nursing unit, not limited to one. Crucially, medical oxygen must be calculated for 100% simultaneous usage. | IfcSpace_M1, Equipment_WaterDispenser_M1, MEP_Gas_M1 | Clause 3.0.1 of T/CECS 1206-2022, Clause 7.3.6 of T/CECS 1206-2022, Clause 9.0.4 of T/CECS 661-2020
289 | Level-3 | Can the facility skip providing storage boxes and bedside tables if they install only one power socket per bed and mandate the use of battery-powered bedside lamps? | No. Providing a bedside table, storage box, and trash can is mandatory. Beds must have three 220V sockets (not one). Bedside lamps are expected to be powered by these designated bedside sockets, not forced to use batteries. | Equipment_Bed_M1, MEP_Power_M1, MEP_Light_M1_2 | Clause 4.1.3.4 of WS 694-2020, Clause 9.5.6 of T/CECS 1206-2022, Clause 9.7.6 of T/CECS 1206-2022
290 | Level-3 | Can we omit the USB port on the bedside sockets, place overhead lights directly above the patient, and provide only medical air without oxygen terminals? | No. The three bedside sockets should include a USB port. Overhead lights must not be placed directly above the bed to prevent glare. Most critically, each bed must have 2 medical oxygen terminals; medical air alone is insufficient. | MEP_Power_M1, MEP_Light_M1_1, MEP_Gas_M1 | Clause 9.5.6 of T/CECS 1206-2022, Clause 9.7.3 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020
291 | Level-3 | Is it compliant to mix genders in a 70-bed zone, skip installing drinking water points, and size the oxygen system at 80% usage capacity? | No. Bed zones must be strictly gender-separated and capped at 50 beds (not 70 mixed). Dedicated drinking water points are mandatory for each nursing unit. Oxygen systems must be sized for 100% simultaneous usage. | IfcSpace_M1, Equipment_WaterDispenser_M1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 7.3.6 of T/CECS 1206-2022, Clause 9.0.4 of T/CECS 661-2020
292 | Level-3 | By ignoring the peacetime usage assessment, can we skip installing public cleaning sockets and reduce the vacuum terminals to zero per bed? | No. Pre-conversion assessment to protect peacetime utility is a core mandate. Public areas explicitly require dedicated electrical sockets for cleaning. Medically, beds require at least 1 vacuum terminal (cannot be reduced to zero). | IfcSpace_M1, MEP_Power_C1, MEP_Gas_M1 | Clause 3.0.1 of T/CECS 1206-2022, Clause 9.5.6 of T/CECS 1206-2022, Clause 9.0.3 of T/CECS 661-2020
293 | Level-3 | To maximize capacity, can beds be placed 0.8m apart, use the peacetime glare-inducing lights without modification, and assume only 30% of patients need oxygen simultaneously? | No. Bed spacing cannot be reduced to 0.8m (must be >1.2m). Glare-inducing peacetime lights must be separately modified or replaced to protect patients. Oxygen systems must be rigorously designed for 100% simultaneous utilization, not 30%. | Equipment_Bed_M1, MEP_Light_M1_1, MEP_Gas_M1 | Clause 4.1.3.4 of WS 694-2020, Clause 9.7.3 of T/CECS 1206-2022, Clause 9.0.4 of T/CECS 661-2020
294 | Level-3 | Can the outdoor generator bypass the exterior wall sleeves, feed directly into Corridor C1 instead of the total distribution room, and require manual shutoff when grid power recovers? | No. Cables must route through reserved exterior wall sleeves. Generator power must feed into the total distribution room (not specific zones directly). When grid power recovers, the generator must perform an automatic delayed shutdown, not manual. | MEP_Generator_Outdoor, Boundary_W7, MEP_ElecRoom | Clause 9.6.3 of T/CECS 1206-2022, Clause 9.5.1 of T/CECS 1206-2022, Clause 9.4.2 of T/CECS 1206-2022
295 | Level-3 | Is it permissible to rely solely on the 15-second generator for the M1 PCR equipment without a UPS, risking a 45-minute blackout for key areas and failing the 24h uninterrupted power mandate? | No. PCR equipment requires <0.5s restoration via a UPS; a 15-second generator is too slow. Key areas must have power restored within 30 minutes (not 45), and the overarching 24h uninterrupted power rule cannot be violated. | MEP_UPS_M1, MEP_Generator_Outdoor, IfcSpace_M1 | Clause 9.4.4 of T/CECS 1206-2022, Clause 8.0.2 of T/CECS 661-2020, Clause 12.0.9 of T/CECS 1206-2022
296 | Level-3 | Can the main hall share an ungraded load circuit simultaneously with the peacetime mall's lighting, instead of properly supplementing power with an outdoor box substation? | No. Electrical loads must be graded by reliability (not ungraded). Circuits cannot be simultaneously shared; if shared, they must be exclusively used for the shelter during epidemics. Insufficient power must be formally supplemented via substations/generators. | MEP_Power_M1, MEP_Power_C1, MEP_Generator_Outdoor | Clause 9.2.1 of T/CECS 1206-2022, Clause 9.3.3 of T/CECS 1206-2022, Clause 9.3.2 of T/CECS 1206-2022
297 | Level-3 | For a retrofit, can the facility pull just a single power line, exclude the medical vacuum from the generator's load calculation, and allow the generator 30 seconds to auto-start? | No. Retrofits must pull dual lines (one being emergency). Critical systems like the medical vacuum must be included in the emergency generator's capacity. The diesel generator must automatically start within 15 seconds, not 30 seconds. | MEP_Power_Main, MEP_Gas_M1, MEP_Generator_Outdoor | Clause 8.0.1 of T/CECS 661-2020, Clause 8.0.2 of T/CECS 661-2020, Clause 9.4.2 of T/CECS 1206-2022
298 | Level-3 | Lacking dual power, can the facility bypass installing a UPS for the <0.5s rescue equipment and route grid power directly to the ward panels, skipping the total distribution room? | No. If lacking dual power, emergency setups are required. Rescue equipment demands <0.5s restoration and strictly requires a UPS. All grid and generator power must route into a total distribution room before feeding local ward panels. | MEP_Power_Main, MEP_UPS_M1, MEP_ElecRoom | Clause 9.3.1 of T/CECS 1206-2022, Clause 9.4.4 of T/CECS 1206-2022, Clause 9.5.1 of T/CECS 1206-2022
299 | Level-3 | Can the 15-second generator exclude M1's HVAC to save capacity, share the emergency circuit with standard peacetime functions, and take 1 hour to restore power to key medical areas? | No. The generator capacity must cover medical HVAC. Emergency circuits must be strictly independent or exclusive during the epidemic. Restoring emergency power to key areas must be completed within 30 minutes, not 1 hour. | MEP_HVAC_M1, MEP_Power_M1, IfcSpace_M1 | Clause 8.0.2 of T/CECS 661-2020, Clause 9.3.3 of T/CECS 1206-2022, Clause 12.0.9 of T/CECS 1206-2022
300 | Level-3 | Can the retrofit project pull two low-voltage lines but skip installing the >30min UPS for the rescue room, while completely sealing the exterior walls without leaving any cable sleeves? | No. Pulling two lines is compliant, but failing to install the UPS for the rescue equipment (which requires <0.5s restoration and ≥30min backup) is a violation. Additionally, exterior walls must reserve cable sleeves for outdoor equipment; they cannot be completely sealed. | MEP_Power_Main, MEP_UPS_M1, Boundary_W7 | Clause 8.0.1 of T/CECS 661-2020, Clause 9.4.4 of T/CECS 1206-2022, Clause 9.6.3 of T/CECS 1206-2022

## Table S6
Table S6. Repeatability testing results across three independent runs.
Difficulty level | Configuration | FDA | ERR | EPR
Overall | B0 | 96.33 ± 0.67 | 97.17 ± 0.36 | 96.22 ± 0.54
| B1 | 58.67 ± 2.00 | 59.86 ± 1.31 | 44.55 ± 2.18
| B2 | 85.00 ± 1.33 | 88.33 ± 1.03 | 79.28 ± 1.37
| B3 | 75.33 ± 2.33 | 86.06 ± 1.58 | 65.89 ± 2.03
Level-1 | B0 | 99.00 ± 0.00 | 98.00 ± 0.50 | 96.50 ± 0.42
| B1 | 68.00 ± 1.00 | 67.50 ± 1.00 | 54.50 ± 1.84
| B2 | 88.00 ± 1.00 | 92.00 ± 1.00 | 91.50 ± 0.95
| B3 | 82.00 ± 2.00 | 90.00 ± 1.50 | 71.50 ± 1.66
Level-2 | B0 | 97.00 ± 1.00 | 97.50 ± 0.25 | 96.00 ± 0.68
| B1 | 63.00 ± 2.00 | 60.75 ± 1.25 | 44.25 ± 2.45
| B2 | 87.00 ± 1.00 | 90.00 ± 0.75 | 76.50 ± 1.42
| B3 | 76.00 ± 2.00 | 87.50 ± 1.25 | 61.50 ± 1.95
Level-3 | B0 | 93.00 ± 1.00 | 96.00 ± 0.33 | 96.17 ± 0.81
| B1 | 45.00 ± 3.00 | 51.33 ± 1.67 | 34.90 ± 2.87
| B2 | 80.00 ± 2.00 | 83.00 ± 1.33 | 79.83 ± 1.76
| B3 | 68.00 ± 3.00 | 80.67 ± 2.00 | 64.67 ± 2.38
Note: All performance metrics are reported as Mean ± Standard Deviation (%) over three independent evaluations.

## Table S7
Table S7. Profiles of the independent experts for blind evaluation
No. | Working years | Department | Position
F1 | 18 | Department of infrastructure development in a hospital | Senior engineer
F2 | 17 | Emergency management bureau | Senior engineer
F3 | 19 | Large-scale building design company | Senior engineer
F4 | 23 | Large-scale building construction company | Senior engineer
F5 | 22 | University | Professor

## Table S8
Table S8. Performance comparison of different foundational LLMs across the testing set
Foundational LLM | Configuration | FDA | ERR | EPR
DeepSeek-V3 | B0 (DSS of this study) | 95.33% | 97.28% | 96.2%
| B1 (No Spatial KG) | 61.33% | 63.52% | 46.12%
| B2 (No Regulatory KG) | 85.67% | 88.21% | 79.46%
| B3 (Single LLM) | 79.67% | 86.35% | 68.17%
Llama-3.3-70B | B0 (DSS of this study) | 93.67% | 95.37% | 94.1%
| B1 (No Spatial KG) | 58.33% | 60.69% | 44.62%
| B2 (No Regulatory KG) | 83.33% | 86.64% | 75.88%
| B3 (Single LLM) | 74% | 84.2% | 63.24%
Qwen2.5-14B | B0 (DSS of this study) | 91.33% | 93.19% | 92.53%
| B1 (No Spatial KG) | 52.67% | 56.46% | 38.48%
| B2 (No Regulatory KG) | 77.33% | 81.77% | 67.59%
| B3 (Single LLM) | 65.67% | 78.41% | 55.82%

## Table S9
Table S9. Quantitative performance comparison of FDA, ERR, and EPR among different multi-agent architectures
Multi-agent architecture | Metric | Level-1 | Level-2 | Level-3 | Overall
Proposed Dual-track MAS | FDA | 99% | 97% | 93% | 96.33%
| ERR | 98% | 97.5% | 96% | 97.17%
| EPR | 96.5% | 96% | 96.17% | 96.22%
Sequential Pipeline MAS | FDA | 96% | 89% | 81% | 88.67%
| ERR | 95% | 88.5% | 82.17% | 88.56%
| EPR | 84.62% | 73.18% | 55.47% | 71.09%
Multi-Agent Debate | FDA | 94% | 91% | 87% | 90.67%
| ERR | 93% | 89.5% | 87.83% | 90.11%
| EPR | 89.34% | 85.12% | 81.76% | 85.41%
Note: All architectures were evaluated using the same 300-query benchmark dataset and GPT-4o foundational model. All performance metrics are reported as the mean over three independent evaluations.